This master should be used by designers working on Port of Portland construction projects and by designers working for PDX tenants (“Tenants”).  Usage notes highlight a few specific editing choices, however the entire section should be evaluated and edited to fit specific project needs.

SECTION 230590 - PRESSURE TESTING OF HVAC SYSTEMS

GENERAL

DESCRIPTION

This section describes pressure testing of piping and ductwork systems.

RELATED WORK SPECIFIED ELSEWHERE

Section 230518, Expansion Compensation

Section 232400, Prefabricated Piping Systems

SUBMITTALS

Submit the following:

Test plan and schedule:  For piping and ductwork systems.

Test Reports:

Certificate of completion, inspection, and test by authority having jurisdiction on required piping systems.

Certificate of test approval to the Port on all systems.

Use only if Commissioning Section 019100 is included in the project manual.

Coordinate with commissioning plan and schedule.

QUALITY ASSURANCE

Code Compliance:  Perform required tests in the presence of the authority having jurisdiction.

Port Witness:  Perform all tests in the presence of the Port.

Simultaneous Testing:  Test observations by the authority having jurisdiction and the Port need not occur simultaneously.

PRODUCTS

Not Used.

EXECUTION

GENERAL

Piping:  Test prior to concealment, insulation being applied, and connection to equipment, fixtures, or specialties.  Conduct tests with all valves but those used to isolate the test section 10 percent closed.

Ductwork:  Test prior to connection to equipment and before applying insulation.

Leaks:  Repair all leaks and retest until stipulated results are achieved.

Notification:  Provide the Port 48 hours notice in advance of each test.  Failure to so notify will require test to be rescheduled.

Testing Equipment:  Provide all necessary pumps, gauges, connections and similar items required to perform the tests.

The Port does not allow pressure testing or pre-testing of chilled water, heating water, steam, condensate, pumped condensate, condenser water, or other hydronic systems, with air or other compressible fluid, at any pressure.

TESTING REQUIREMENTS

Medium Pressure Ductwork:

Test all systems at 4-inch static pressure, using a Pacific Air Products Port-O-Lab, Rolok, or equal testing machine.

Maximum allowable leakage percentage is defined as CFM air leakage per cubic foot volume of duct section tested.  This is not percentage of design air flow.  Leakage shall not be greater than 10 percent of duct volume per minute.

Piping:  Test all piping as noted below, with no leaks or loss in pressure for time indicated.  Repair or replace defective piping until tests are completed successfully:

| System | Test Pressure | Test Medium | Test Duration |
| --- | --- | --- | --- |
| Chilled water | 150 psig | water | 4 hours |
| Heating water | 150 psig | water | 4 hours |
| Condenser water | 150 psig | water | 4 hours |
| Steam and condensate | 100% of system-design pressure | water | 4 hours |
| Refrigerant piping | 300 psig | nitrogen | 4 hours |

Prefabricated Piping Systems:  Test in accordance with the requirements of Section 232400, Prefabricated Piping Systems.

Piping Systems with Expansion Compensation:  Test in accordance with the requirements of Section 230518, Expansion Compensation.

END OF SECTION 230590