This master should be used by designers working on Port of Portland construction projects and by designers working for PDX tenants (“Tenants”).  Usage notes highlight a few specific editing choices, however the entire section should be evaluated and edited to fit specific project needs.

This master is specific to the PDX and HIO terminal buildings.  Projects that do not tie into this control system should not use this master.  Contact the facilities group to determine which projects are appropriate for this master.

SECTION 230900 - INSTRUMENTATION AND CONTROLS FOR HVAC

GENERAL

description

Furnish and install a complete facility management system (FMS) for all mechanical systems and other facility systems as included in the contract documents.  The system shall perform all sequences of operations stated within these specifications or shown on the drawings.

RELATED WORK SPECIFIED ELSEWHERE

Section 221120, Plumbing Pumps

Section 230500, Common Work Results for HVAC

Section 230553, Identification for HVAC Piping and Equipment

Section 230593, Testing, Adjusting, and Balancing

Section 232220, HVAC Pumps

Section 232923, Variable-Frequency Motor Controllers

Section 233300, Air Duct Accessories

Section 233400, HVAC Fans

Section 233600, Air Terminal Units

Section 235200, Heating Boilers and Accessories

Section 235500, Fuel-Fired Heaters

Section 235523, Gas-Fired Radiant Heater

Section 235700, Heat Exchangers for HVAC

Section 236400, Packaged Water Chillers

Section 237000, Central HVAC Equipment

Section 238100, Decentralized Unitary HVAC Equipment

Section 238116, Computer Room Air Conditioners

Section 283100, Fire Detection and Alarm

REFERENCES

ASHRAE:  American Society of Heating, Refrigerating and Air-Conditioning Engineers

ASHRAE Chapter 62: Ventilation for Acceptable Indoor

FCC:  Federal Communications Commission

FCC Part 15: Radio Frequency Devices

ISO:  International Organization for Standardization

ISO 9001: Quality Management Systems - Requirements

NEC:  National Electric Code

NEMA:  National Electrical Manufacturers’ Association

REA:  Rural Electrification Administration

REA PE-60d: RUS Specification for Trunk Carrier Systems

UL:  Underwriters Laboratories

US EPA:  US Environmental Protection Agency

Energy Star Building Recommendations

SUBMITTALS

For systems, equipment, and components specified herein, submit product/material data; certified shop drawings; installation, startup, and testing manuals; operation and maintenance data; as-constructed data; operation and maintenance manuals; and as-constructed drawings.

System Drawings and Schedules:  Include the following:

Direct digital control (DDC) panel physical layout and schematics.

One-line schematics and system flow diagrams showing the location of all control devices.  Provide points list for each DDC controller, including tag, point type, system name, object name, expanded ID, controller type, address, cable destination, terminal ID, panel, reference drawing, and cable number.

Details of connections to power sources, including grounding.

Details of surge protection device installations.

Sequences of operation.

Complete diagrams of the related pneumatic and electric controls, including a written description of control sequences.

User interface (UI) functional outline.  Include each display screen to be provided, data to be displayed, and links to other screens.  The outline level hierarchy shall be:

Site.

Building.

Floor.

System.

Control Damper and Valve Schedules:  Include code number, failure position, pipe or duct size, valve or damper size, damper seal, blade and bearing type, valve body configuration, CV, flow, pressure drop and close-off pressure.

Prototype graphics for review prior to implementation of the full graphics package.

Delete the following subparagraph and all its items if work is not at PDX.

PDX System Master Plan:

Upon completion of the work, update the PDX systems master plan to reflect the as-constructed configuration of the DDC control system.

Submit in the operation and maintenance manual the portion of updated master plans related to this work.

Equipment Data:  Include complete data for all materials, including field and system equipment.  Data provided shall be marked to indicate which specific model or feature will be provided.

Field Installation Handbook:  Show all standard devices, networks, controllers, and enclosures with configurations, cable specifications, wiring and installation methods, termination details, agency listings, and controller specifications.

Software Data:  Provide complete descriptions of system, command, and applications software as specified.  Include description of control sequences which are software based using detailed logic flow diagrams.  Diagrams shall indicate logic used to achieve control sequence of calculation specified, and shall show relationship between control sequence and application software packages specified.

Operation and Maintenance Manuals:  Provide three complete sets of manuals bound in loose-leaf binders within 30 days after completing acceptance tests.  Manuals shall include names, addresses, and telephone numbers of each subcontractor installing equipment and systems, and of nearest service representatives for each item of equipment and each system.  Final copies delivered after completion of the acceptance tests shall include all modifications made during installation, checkout, and acceptance.  Operation and maintenance manuals shall include the hardware manual, software manual, operations manual, maintenance manual, and portion of updated master plans related to this work.

Hardware Manual:  Describe all equipment provided, including:

General description and specifications.

Field Installation Handbook:  Show all standard devices, networks, controllers and enclosures with configurations, cable specifications, wiring and installation methods, termination details, agency listings and controller specifications.

As-built system drawings and schedules.

Alignment and calibration procedures.

Software Manual:  Describe all furnished software.  Include the following documentation in the DDC software manual:

Sequence of operations.

Program listing of software source code and flow chart diagrams of programming objects for all major systems.

Printed listing of controller and operator workstation database files.

Software point name abbreviation list.  Include name, description, controller where located, point type and point ID.

Input/output (I/O) point list.  Include point name, controller location, point number, control device, range and span.

Printouts of all reports, group listings, and alarm messages.

Operator’s Manual:  Provide all procedures and instructions for operation of the system, including:

DDC panels and peripherals.

System startup and shutdown procedures.

Use of system, command, and applications software.

Alarm presentation.

Recovery and restart procedures.

Report generation.

System schematic graphics.

Maintenance Manual:  Provide descriptions of maintenance for all equipment including inspection, periodic preventive maintenance, fault diagnosis, and repair or replacement of defective components.

Coordinate the following paragraph with Section 019100, General Commissioning Requirements.

For system, equipment, and components, submit commissioning plans and schedules; checkout, startup, operational, functional and final acceptance test plans, procedures, checklists, and reports; systems manuals; and operation and maintenance training plans.

Testing Submittals:  Provide test plan and test procedures for approval.  Explain in detail, step-by-step, actions and expected results to demonstrate compliance with the requirements of this specification and methods for simulating necessary conditions of operation to demonstrate performance of the system.  Test plan and test procedures shall demonstrate capability of system to monitor and control equipment and to accomplish control and monitoring specified.

QUALITY ASSURANCE

General:

The FMS installer shall be a factory-owned branch office that is regularly engaged in the engineering, programming, installation, and service of FMSs of similar size and complexity.

The FMS, including all components and appurtenances, shall be configured and installed to yield a mean time between failures of at least 1,000 hours.

ISO-9001:

Provide documentation supporting compliance with ISO-9001 (Model of Quality Assurance in Design/ Development, Production, Installation, and Servicing).  Product literature shall contain the ISO-9001 Certification Mark from the applicable registrar.  For products that do not comply with the ISO-9001 certification requirement, provide the following information to assure that quality systems are in place which are equivalent to the ISO-9001 standard:

Marketing specification standards.

Design file standards.

Manufacturing test standards.

Calibration standards.

Quality system standards.

Quality system procedures.

Documented management commitment that all employees participate in quality programs.

Training procedures.

Methods by which corrective actions are taken for problems identified within the factory process.

FCC Regulation:

All electronic equipment shall conform to the requirements of FCC Regulation, Part 15, Section 15, Governing Radio Frequency Electromagnetic Interference, and be so labeled.

UL:

Components shall be UL listed or recognized under the appropriate standard.  These standards may include:

UL 916 for energy management systems.

UL 864 for fire, smoke and process control systems, as required.

UL 873 for controllers and temperature indicating and regulating equipment.

COMMISSIONING AND TRAINING

Systems, equipment and component checkout, startup, calibration, operational, functional and final acceptance testing:

General:  Provide all personnel, equipment, instrumentation, and supplies necessary to commission controls.

Commissioning:  Commission systems, equipment, and components in accordance with the requirements of the contract documents.  Demonstrate compliance of completed control system.  Checkout and test all physical, operational, and functional requirements of the controls and related equipment.

Callbacks:  In addition to the requirements of the contract, the Port may request, at its discretion, a recheck or resetting of any equipment, device or control on two occasions within the first year of operation.

Training:

General:  Conduct training courses for designated personnel in operation and maintenance of system.  Orient training to specific system being installed.  Provide training manuals for each trainee, with two additional copies provided for archival at work site.  Manuals shall include detailed description of the subject matter for each lesson.  Deliver copies of audiovisuals to the Port.

Operator’s Training:  The course shall be taught at the work site for a period of one training day after completion of the Contractor’s field testing.  The course shall include instruction on specific hardware configuration of installed system and specific instructions for operating the installed system.  Upon completion, each student shall be able to start system, operate the system, recover the system after failure, and describe the specific hardware architecture and operation of system.  Repeat course if necessary to include all shift personnel.

PRODUCTS

MANUFACTURER

The FMS architecture shall consist of the products of a manufacturer regularly engaged in the production of FMS, and shall be the manufacturer’s latest standard of design.  Controllers and DDC system components shall be current production products.

All other equipment shall be the products of the FMS manufacturer or of an approved manufacturer regularly engaged in production of specialized FMS materials or equipment.

Per Port’s Contract Review Board Rules adopted Nov. 12, 2003, Johnson Controls’ Metasys Facility Mgmt./Building Automation Control System and components are an approved “no substitution” exemption when used at PDX and ancillary surrounding campus buildings, which are integrated into the C.U.P.’s networked FMS system.  Exemption expires 1/9/2025.

Acceptable FMS Manufacturer:  Johnson Controls Group, Inc., Milwaukie, OR, no substitutions.  Phone: (503) 305-2000.

SYSTEM DESCRIPTION

First-Tier Network:

The automation network shall be based on a personal computer (PC) industry standard of Ethernet TCP/IP.  Where used, LAN controller cards shall be standard “off-the-shelf” products available through normal PC vendor channels.

The FMS shall network multiple UI clients, automation engines, system controllers and application-specific controllers (ASC).  Provide application and data server(s) as required for systems operation.

All FMS devices on the automation network shall be capable of operating at a communication speed of 100 Mbps, with full peer-to-peer network communication.

Network automation engines (NAE) shall reside on the automation network.

The automation network shall be compatible with other enterprise-wide networks. Where indicated, the automation network shall be connected to the enterprise network and share resources with it by way of standard networking devices and practices.

Second-Tier Network:

NAE shall provide supervisory control over the control network and shall support all three of the following communication protocols:

BACnet Standard Master-Slave Token Passing (MS/TP) Bus Protocol ASHRAE SSPC-135, Clause 9.

The NAE shall be BACnet Testing Labs (BTL) certified and carry the BTL Label.

The NAE shall be tested and certified as a BACnet Building Controller.

LonWorks enabled devices using the Free Topology Transceiver (FTT-10a).

The Johnson Controls N2 Field Bus.

The Johnson Controls wireless field bus.

Control networks shall provide peer-to-peer, master-slave, or supervised token passing communications, and shall operate at a minimum communication speed of 9600 baud.

DDC Controllers shall reside on the control network.

Control network communication protocol shall be BACnet Standard MS/TP Bus Protocol ASHRAE SSPC-135.

A BACnet Protocol Implementation Conformance Statement (PICS) shall be provided for each controller device, master or slave, which will communicate on the BACnet MS/TP Bus.

Integration Options:

Hardwired:

Analog and digital signal values shall be passed from one system to another via hardwired connections.

There shall be one separate physical point on each system for each point to be integrated between the systems.

Wireless:

Series Wireless Field Bus System: Series system shall employ ZigBee technology that creates a wireless mesh network to provide wireless connectivity for Metasys BACnet devices at multiple system levels.  This includes communications from field equipment controller and VAV modular assembly (VMA) field controllers to sensors and from engines to these field controllers.  Wireless devices shall co-exist on the same network with hardwired devices.  Hardwired controllers shall be capable of retrofit to wireless devices with no special software.

Direct Protocol (Integrator Panel):

The FMS system shall include appropriate hardware equipment and software to allow bi-directional data communications between the FMS system and third-party manufacturers’ control panels.  The FMS shall receive, react to, and return information from multiple building systems, including but not limited to the chillers, boilers, variable frequency drives, power monitoring system, and medical gas.

All data required by the application shall be mapped into the NAE database, and shall be transparent to the operator.

Point inputs and outputs from the third-party controllers shall have real-time interoperability with FMS software features such as: control software, energy management, custom process programming, alarm management, historical data and trend analysis, totalization, and local area network communications.

BACnet Protocol Integration – BACnet:

The neutral protocol used between systems shall be BACnet over Ethernet and comply with the ASHRAE BACnet standard 135-2008.

A complete PICS shall be provided for all BACnet system devices.

Provide the ability to command, share point object data, change of state (COS) data and schedules between the host and BACnet systems.

Server/Web Browser/Operator Interfaces:

Dedicated Web-Based UI:

Where indicated on the drawings, provide a PC for command entry, information management, network alarm management, and database management functions. All real-time control functions including scheduling, history collection, and alarming shall be resident in the NAE to facilitate greater fault tolerance and reliability.

Dedicated UI Architecture:  The architecture of the computer shall be implemented to conform to industry standards so that it can accommodate applications provided by the FMS, including but not limited to Microsoft Office applications. Specifically, it shall be implemented to conform to the following interface standards:

Microsoft Internet Explorer for UI functions.

Microsoft Office Professional for creation, modification, and maintenance of reports, sequences, and other necessary building management functions.

Microsoft Outlook or other e-mail program for supplemental alarm functionality and communication of system events and reports.

Required network operating system for exchange of data and network functions such as printing of reports, trends, and specific system summaries.

PC Hardware: The PC(s) shall be configured as follows:

Memory:  1 GB (512 MB minimum).

CPU:  Pentium 4 processor.  2.8 GHz clock speed (2.0 GHz minimum).

Hard Drive:  80 GB free hard drive space (40 GB minimum)

Hard Drive Backup System:  CD/RW, DVD/RW, or network backup software provided by IT department.

CD ROM Drive:  32X performance.

Ports:  2 serial and 1 parallel, 2 USB ports.

Keyboard:  101 keyboard and 2 button mouse.

CRT Configuration:  1-2 CRTs as follows:

Each display shall be 17-inch flat panel monitor, 1280x1024 resolution minimum.

16 bit or higher color resolution.

Display card with multiple monitor support.

LAN Communication:  Ethernet communications board.  3Comm, or equal.

Operating System Software shall be as follows:

Windows 7 or 8 Professional.

Where UI is not provided via browser, provide complete operator workstation software package including any hardware or software keys. Include the original installation disks and licenses for all included software, device drivers, and peripherals.

Provide software registration cards for all included software.

Peripheral Hardware.  Provide reports printer meeting the following requirements:

Printer Make:  Hewlett Packard DeskJet.

Print Speed:  600 DPI black, 300 DPI color.

Buffer:  64 K input print buffer.

Color Printing:  Include color kit.

Distributed Web-Based UI:

All features and functions of the dedicated UI previously defined in this specification shall be available on any computer connected directly or via a wide area or virtual private network (WAN/VPN) to the automation network and conforming to the following:

The software shall run on the Microsoft Internet Explorer (6.0 or higher) browser supporting the following functions:

Configuration.

Commissioning.

Data archiving.

Monitoring.

Commanding.

System diagnostics.

Minimum hardware requirements are as follows:

1 GB RAM.

2.0 GHz clock speed Pentium 4 microprocessor.

100 GB hard drive.

1 keyboard with 83 keys, minimum.

SVGA 1024x768 resolution display with 64K colors and 16 bit color depth.

Mouse or other pointing device.

Site Management UI Application Components:

Operator interface shall meet the following criteria:

Integrated browser-based client applications.

The system shall have event-driven rather than device polling methodology to dynamically capture and present new data to the user.

All inputs, outputs, setpoints, and all other parameters as defined in Part 3 of this section, as shown on the drawings, or as required as part of the system software, shall be displayed for operator viewing and modifying from the operator interface software.

UI software shall provide help menus and instructions for each operation and/or application.

The system shall support customization of the UI configuration and a home page display for each operator.

The system shall support user preferences in the following screen presentations:

Alarm.

Trend.

Display.

Applications.

All controller software operating parameters shall be displayed for the operator to view/modify from the UI.  These include, but are not limited to, setpoints, alarm limits, time delays, PID tuning constants, run-times, point statistics, and schedules.

The operator interface shall incorporate comprehensive support for functions including, but not necessarily limited to, the following:

User access for selective information retrieval and control command execution.

Monitoring and reporting.

Alarm, non-normal, and return to normal condition annunciation.

Selective operator override and other control actions.

Information archiving, manipulation, formatting, display, and reporting.

FMS internal performance supervision and diagnostics.

Online access to user Help menus.

Online access to current FMS as-built records and documentation.

Means for the controlled reprogramming, reconfiguration of FMS operation, and for the manipulation of FMS database information in compliance with the prevailing codes, approvals, and regulations for individual FMS applications.

The system shall support a list of applications programs configured by the users that are called up by the following means:

The Tools menu.

Hyperlinks within the graphics displays.

Key sequences.

The operation of the control system shall be independent of the UI which shall be used for operator communications only.  Systems that rely on an operator workstation to provide supervisory control over controller execution of the sequences of operations or system communications will not be acceptable.

Navigation Trees:

The system shall have the capability to display multiple navigation trees that aids the operator in navigating throughout all systems and points connected.  At a minimum, provide a tree that identifies all systems on the networks.

Provide the ability for the operator to add custom trees.  The operator shall be able to define any logical grouping of systems or points and arrange them on the tree in any order.  Groups shall be able to nest within other groups.  Provide at minimum five levels of nesting.

The navigation trees shall be “dockable” to other displays in the UI, such as graphics.  The trees shall appear as part of the display but can be detached and then minimized to the Windows task bar.  A simple keystroke shall reattach the navigation to the primary display of the UI.

Alarms:

Alarms shall be routed directly from NAE to PCs and servers.  Specific alarms from specific points shall be able to be routed to specific PCs and servers.  The alarm management portion of the UI shall, at minimum, provide the following functions:

Log date and a time of alarm occurrence.

Generate a pop-up window, with audible alarm, informing a user that an alarm has been received.

Allow a user, with the appropriate security level, to acknowledge, temporarily silence, or discard an alarm.

Include the following paragraph if an ADS or ADX will be provided.  Otherwise delete.

Provide an audit trail on hard drive for alarms by recording user acknowledgment, deletion, or disabling of an alarm.  The audit trail shall include the name of the user, the alarm, the action taken on the alarm, and a time/date stamp.

Provide the ability to direct alarms to an e-mail address or alphanumeric pager.  This shall be provided in addition to the pop-up window described in this section.  Systems that use e-mail and pagers as the exclusive means of annunciating alarms are not acceptable.

Configuration of which NAE offline alarms are seen by each user.

Any attribute of any object in the system may be designated to report an alarm.

The FMS shall annunciate diagnostic alarms indicating system failures and non-normal operating conditions.

The FMS shall allow a minimum of four categories of alarm sounds, customizable through user-defined .wav files.

The FMS shall annunciate application alarms at minimum, as required in Part 3 of this section.

Reports and Summaries:

Reports and summaries shall be generated and directed to the UI displays with subsequent assignment to printers, or disk.  At a minimum, the system shall provide the following reports:

All points in the FMS.

All points in each BMS application.

All points in a specific controller

All points in a user-defined group of points

All points currently in alarm

All points locked out

All user defined and adjustable variables, schedules, interlocks, etc.

Summaries and reports shall be accessible via standard UI functions and not dependent upon custom programming or user defined HTML pages.

Selection of a single menu item, tool bar item, or tool bar button shall print any displayed report or summary on the system printer for use as a building management and diagnostics tool.

Provide the capability to view, command, and modify large quantities of similar data in tailored summaries created online without the use of a secondary application, like a spreadsheet.  Summary definition shall allow up to seven user defined columns describing attributes to be displayed, including custom column labels.  At a minimum, 100 rows per summary shall be supported.  Summary viewing shall be available over the network using a standard Web browser.

Include the following paragraph if an ADX will be provided.  Otherwise delete.

Provide a focused set of reports that includes essential information required for effective management of energy resources within the facility.  Energy reports shall be configurable from predefined, preconfigured templates. Requirements include, but is not be limited to:

Energy overview.

Load profile.

Simple energy cost.

Consumption.

Equipment runtime.

Electrical energy.

Energy production.

Reports shall be selectable by day, time, area, and device.  Each report shall include a color visual summary of essential energy information.

Schedules:

Provide a graphical display for time-of-day scheduling and override scheduling of building operations.  At a minimum, the following functions shall be provided:

Weekly schedules.

Exception schedules.

Monthly calendars.

Provide weekly schedules for each group of equipment with a specific time-use schedule.

One or more exception schedules for each schedule, including references to calendars, shall be possible.

Provide monthly calendars that allow for simplified scheduling of holidays and special days for a minimum of five years in advance.  Holidays and special days shall be user-selected with the pointing device or keyboard and shall automatically reschedule equipment operation as previously defined on the exception schedules.

Changes to schedules made from the UI shall directly modify the NAE schedule database.

Schedules and calendars shall comply with ASHRAE SP135/2008 BACnet Standard.

The calendar object shall support an option to add a reference to another calendar object designated to be the master for the facility.  Any supervisory and BAC calendars shall be able to be configured to reference a single master global calendar.  Changes to the master global calendar shall automatically sync with all calendars that are referenced.

Selection of a single menu item or tool bar button shall print any displayed schedule on the system printer for use as a building management and diagnostics tool.

Provide software to configure and implement optimal start and stop programming based on existing indoor and outdoor environmental conditions as well as equipment operating history.

The system solar clock shall support the scheduling and energy management functions.  The solar clock shall calculate the sunrise, sunset, and sun angle values for a specified latitude and longitude.  A time offset may also be specified.  An example would be to use the solar clock object as a master to an interlock to turn lights on 30 minutes after sunset and off 30 minutes before sunrise.

Security/Passwords:

Provide multiple-level password access protection via roles and permissions.  The feature shall allow the system to base access on a user’s job title or role and allow the user/manager access interface control, display, and database manipulation capabilities based on an assigned password.

Roles may be copied and altered to meet specific roles and permissions based on the particular policies.

Each user shall have the following: a (Metasys Local) user account name (with a maximum of 30 characters), a complex password or passphrase (with a min of 8 characters and a max of 50 characters), other user account policies (such as session timeout), timesheet access based on day of the week and time of day, and specific user view.

The system shall allow each user to change his or her password at will.

When entering or editing passwords, the system shall not echo the actual characters for display on the monitor.

A maximum of 150 categories may be used to determine or assign areas of responsibilities to each user account.  A maximum of 13 of the 150 named categories, shall be specifics such as, “No Access,” “View,” “Advanced Review,” “Operate,” “Intervene,” “Diagnostic,” “Manage Item Events,” “Manage Every,” and “Configure Items.”

A minimum of 100 unique passwords shall be supported.

Operators shall be able to perform only those commands available for their respective passwords.  Display of menu selections shall be limited to only those items defined for the access level of the password used to log-on.

Operators shall be further limited to only access, command, and modify those buildings, systems, and subsystems for which they have responsibility.  Provide a minimum of 100 categories of systems to which individual operators may be assigned.

The system shall automatically generate a report of log-on/log-off and system activity for each user.  Any action that results in a change in the operation or configuration of the control system shall be recorded, including, but not limited to: modification of point values, schedules or history collection parameters, and all changes to the alarm management system, including the acknowledgment and deletion of alarms.

The system shall have the ability to provide a Department of Defense specific warning banner for applicable sites that warns the user they are accessing a restricted site.

After successful login to the Site Management Portal, the last time and date that user name was previously logged in shall be shown on the screen.

Each login attempt shall be recorded in the system audit log with the option to record the IP address of the PC that made the login.

Screen Manager:

The system shall allow a customized image on the login screen (i.e., organization name, logo).

User view navigations may be displayed as either a set of tabs or a drop down list.

Allow users a preference for assigning a background color for when an object is out of service which will enable the operator to quickly distinguish points that have been commanded to this state.

Provide the UI with screen management capabilities that allow the user to activate, close, and simultaneously manipulate a minimum of four active display windows plus a network or user defined navigation tree.

Dynamic Color Graphics:

The graphics application program shall be supplied as an integral part of the UI. Browser or workstation applications that rely only upon HTML pages will not be acceptable.

The graphics applications shall include a create/edit function and a runtime function.  The system architecture shall support an unlimited number of graphics documents (graphic definition files) to be generated and executed.  The graphics shall be able to display and provide animation based on real-time data that is acquired, derived, or entered.

Graphics Runtime Functions:  A maximum of 16 graphic applications shall be able to execute at any one time on a UI or workstation, with 4 visible to the user.  Each graphic application shall be capable of the following functions:

All graphics shall be fully scalable.

The graphics shall support a maintained aspect ratio.

Multiple fonts shall be supported.

Unique background shall be assignable on a per graphic basis.

The color of all animations and values on displays shall indicate the status of the object attribute.

Graphics that represent buildings or systems shall allow natural links and transitions between related detailed tabular views of data that complement the graphic.

Operation from Graphics:  Values (setpoints) and states shall be able to change in system controlled equipment directly from the graphic.

Floor Plan Graphics:  The UI shall provide graphic applications that summarize conditions on a floor.  Floor plan graphics shall indicate thermal comfort using dynamic colors to represent zone temperature deviations from zone setpoint(s) and shall display overall metrics for each zone in the floor.

Aliasing:  Many graphic displays representing part of a building and various building components are exact duplicates, with the exception that the various variables are bound to different field values.  Consequently, the value of a graphic display shall bind to aliases instead of the physical field tags.

Graphic Editing Tool:  A graphic editing tool shall allow for the creation and editing of graphic files. The graphic editor shall be capable of performing/defining all animations, defining all runtime binding, and shall provide the following:

A library of standard HVAC equipment, floor plan, lighting, security, and network symbols.

For the creation and positioning of library symbols by dragging from tool bars or drop-downs and positioning, where required.

Ability to import AutoCAD drawings for use in the system.

Ability to add additional content to any graphic by importing images in the SVG, PNG, or JPG file formats.

Historical Trending and Data Collection:

Each NAE shall store trend and point history data for all analog and digital inputs and outputs, as follows:

Any point, physical or calculated, may be designated for trending. Two methods of collection shall be allowed: defined time interval or upon a change of value.

Capacity to store multiple samples for each physical point and software variable based upon available memory, including an individual sample time/date stamp. Points may be assigned to multiple history trends with different collection parameters.

Trend and change of value data shall be stored within the engine and upload to a dedicated trend database or exported in a selectable data format via a provided data export utility. Uploads to a dedicated database shall occur based upon one of the following: user-defined interval, manual command, or when the trend buffers are full. Exports shall be as requested by the user or on a time-scheduled basis.

The system shall provide a configurable data storage subsystem for the collection of historical data. Data can be stored in SQL database format.

The system shall provide data to enable optimization capabilities including fault detection and diagnostics, advanced analytics, and central plant optimization without the need of a gateway or additional hardware.

Trend Data Viewing and Analysis:

Provide a trend viewing utility that shall have access to all database points.

Retrieving any historical database point for use in displays and reports shall be possible by specifying the point name and associated trend name.

The trend viewing utility shall have the capability to define trend study displays to include multiple trends.

Displays shall be single or stacked graphs with online selectable display characteristics such as ranging, color, and plot style.

Display magnitude and units shall both be selectable by the operator at any time without reconfiguring the processing or collecting data.  This shall be a zoom capability.

Display magnitude shall automatically be scaled to show full graphic resolution of the data being displayed.

The display shall support the user’s ability to change colors, sample sizes, and types of markers.

Database Management:

Where a separate SQL database is utilized for information storage, the system shall provide a database manager that separates the database monitoring and managing functions by supporting two separate windows.

Database secure access shall be accomplished using standard SQL authentication, including the ability to access data for use outside of the building automation application.

The database managing function shall include summarized information on trend, alarm, event, and audit for the following database management actions:

Backup.

Purge.

Restore.

The database manager shall support four tabs:

Statistics.  Display database server information and trend, alarm (event), and audit information on the Metasys databases.

Maintenance.  Provide an easy method of purging records from the Metasys server trend, alarm (event), and audit databases by supporting separate screens for creating a backup prior to purging, selecting the database, and allowing for the retention of a selected number of day’s data.

Backup.  Provide the means to create a database backup file and select a storage location.

Restore.  Provide a restricted means of restoring a database by requiring the user to log into an expert mode in order to view the restore screen.

The status bar shall appear at the bottom of all Metasys database manager tabs and shall provide information on the current database activity.  The following icons shall be provided:

Ready.

Purging record from a database.

Action failed.

Refreshing statistics.

Restoring database.

Shrinking a database.

Backing up a database.

Resetting internet information services.

Starting the Metasys device manager.

Shutting down the Metasys device manager.

Action successful.

Access the database manager monitoring functions through the monitoring settings window and continuously read database information once the user has logged in.

The system shall provide user notification via taskbar icons and e-mail messages when a database value has exceeded a warning or alarm limit.

The monitoring settings window shall have the following sections:

General.  Allows the user to set and review scan intervals and start times.

Email.  Allows the user to create and review e-mail and phone text messages to be delivered when a warning or alarm is generated.

Warning.  Allows the user to define the warning limit parameters, set the reminder frequency, and link the e-mail message.

Alarm.  Allows the user to define the alarm limit parameters, set the reminder frequency, and link the e-mail message.

Database login.  Protects the system from unauthorized database manipulation by creating a read access and a write access for each trend, alarm (event), and audit database as well as an expert mode required to restore a database.

The monitoring settings taskbar shall provide the following informational icons:

Normal.  Indicates by color and size that all databases are within their limits.

Warning.  Indicates by color and size that one or more databases have exceeded their warning limit.

Alarm.  Indicates by color and size that one or more databases have exceeded their alarm limit.

The system shall provide user notification via taskbar icons and e-mail messages when a database value has exceeded a warning or alarm limit.

Demand Limiting and Load Rolling:

The system shall provide a demand limiting and load rolling program for the purpose of limiting peak energy usage and reducing overall energy consumption.

The system shall support both sliding window and fixed window methods of predicting demand.

The system shall support three levels of sensitivity in the sliding window demand calculations for fine tuning the system.

Low setting.  Sheds loads later and over the shortest amount of time.  Maximizes the time the equipment is on.

Medium setting.  Sheds loads earlier over a longer amount of time than the low setting.  Increases the time the equipment is on and decreases the probability of exceeding the tariff target over the low setting.

High Setting.  Sheds loads earlier over a longer amount of time than the medium setting.  Minimizes the probability of exceeding the tariff target.

The system shall have a “Shed” mode and a “Monitor Only” mode of operation.

When the shed mode is engaged, the system shall actively control the demand.

When the monitor mode is engaged, the system shall simulate the shedding action but shall not take any action.

The demand limiting program shall monitor the energy consumption rate and compare it to a user-defined tariff target.  The system shall maintain consumption below the target by selectively shedding loads based upon a user-defined strategy.

The demand limiting program shall be capable of supporting a minimum of 10 separate load priorities.  Each load shall be user assigned to a load priority.

The demand limiting program shall be capable of supporting a minimum of 12 separate tariff targets defining the maximum allowed average power during the current interval.

The system shall support a maximum shed time for each load as determined by the user.  The system shall restore the load before the maximum shed time has expired.

The system shall support a minimum shed time for each load as determined by the user.  The system shall not restore the load sooner than the minimum shed time has expired.

The system shall support a minimum release time for each load as determined by the user.  The system shall not shed the load until it has been off for the minimum release time.

The system shall support three user-defined options if the meter goes unreliable.

Shedding.  The currently shed loads shall be released as their maximum shed times expire.

Maintain the current shed rate.  The system shall use the demand limiting shed rate that was present when the meter went unreliable.

Use unreliable meter shed rate.  The system shall control to a user-defined unreliable shed rate target.

The load rolling program shall sum the loads currently shed and compare it to a user-defined load rolling target.  The system shall maintain consumption below the target by selectively shedding loads based upon a user-defined load priority.

The load rolling program shall be capable of supporting a minimum of 10 separate load priorities.  Each load shall be user assigned to a load priority.

The load rolling program shall be capable of supporting a minimum of 12 separate tariff targets defining the amount of power by which the demand shall be reduced.

The system shall provide the user with a load tab that displays all of the demand limiting and load rolling parameters for any selected load.

The system shall provide the user with a load summary that displays all of the loads associated with the demand limiting and load rolling programs.  Status icons for each load shall indicate:

Load is offline.

Load is disabled.

Load is shed.

Load is locked.

Load is comfort override.

The load summary shall include a load summary runtime view listing the following load conditions:

Load priority.

Shed strategy.

Load rating.

Present value.

Ineligibility status.

Active timer.

Time remaining.

Last shed time.

Portable Operator Terminal:

For systems that do not provide full access to system configuration and definition via the browser-based UI, provide a portable operator terminal for programming purposes. The terminal shall be configured as follows:

Personal laptop computer manufacturer:  Dell, Compaq, or HP.

1 GB RAM, 256 MB minimum.  Microsoft Windows 7 or 8 Professional.

1.8 GHz clock speed Pentium 4 microprocessor, 800 MHz minimum.

40 GB Hard Drive, 40 GB minimum.

1 CD-ROM Drive, 32 x speeds.

1 serial, 1 parallel, 2 USB ports.

1 keyboard with 83 keys, minimum.

Integral 2 button track point or track ball.

10-inch SVGA 1024x768 resolution color display.

2 PCMCIA Type II or 1 Type III card slot.

Complete operator workstation software package including any hardware or software.

Original printed manuals for all software and peripherals.

Original installation disks or CD for all software, device drivers, and peripherals.

Software registration cards for all included software.

Carrying case.

Spare battery.

External power supply/battery charge.

Proprietary Portable Terminal:  Submit technical data sheets for the terminal and all associated software and hardware.

Software:

Portable operator terminals shall support all controllers within the system on a direct-connect communications basis.

When used to access first or second tier controllers, the portable operator terminal shall utilize the standard operator workstation software, as defined in this section.

When used to access application specific controllers, the portable operator terminal shall utilize either the standard operator workstation software, as defined in this section, or controller-specific utility software.

Metasys UI:

Provide all computer hardware and software required for the purpose of configuration and consolidation of information and programs required for the delivery of a task focused, web based portal to the FMS.  The Metasys UI shall provide a natural, complementary extension to the Metasys site management UI previously described in this section.

The UI architecture shall be implemented to conform to industry standards, accommodating the required applications and communicating information to and from any size control system.

The exact same UI shall be accessible from any type of PC or mobile device running any type of operating system (i.e., iOS, Android, Windows).

The interface shall automatically adapt and optimize the information displayed to fit the screen size of the client device and shall also be touch friendly.

The UI shall organize and display information using customer-specific locations and spaces.  At a minimum, the UI shall provide:

Organization of all space, equipment, and point information in a familiar way, reducing the need for extensive training prior to use.

A navigation mechanism for users to select the specific location or space to display information for, but only spaces and locations in the navigation tree.

The ability to search for and/or bookmark any location or space by name for quick access to critical or troublesome areas.

The same navigation mechanisms apply across any client device (i.e., smartphone, tablet, PC) for consistency and ease of use.

Plug-ins and special native application software (i.e., downloaded and installed from an app store) shall not be required to conduct daily operations of buildings and equipment.

The UI shall clearly display equipment relationships without custom graphic generation.

The UI shall provide a single display of all potential issues in a facility including items currently in alarm, warning, override, out-of-service, and offline.

The UI shall provide a single display of all activity related to a specific piece of equipment including user changes, discarded user changes, pending alarms, discarded alarms, and acknowledged alarms.

The UI shall provide support for up to 100 concurrent users from an unlimited number of individuals with defined password access to the system.

Provide the capability to view, command, and modify large quantities of similar data in tailored summaries without the use of a secondary application, such as a spreadsheet.  These summaries shall be automatically generated or user-defined.  User-defined summaries shall allow up to seven user-defined columns describing attributes to be displayed, including custom column labels.  Up to 100 rows per summary shall be supported.

Ready Access Portal UI:

Provide all computer hardware and software required for the purpose of configuration and consolidation of information and programs required for the delivery of a task focused, web-based portal to the FMS.  The ready access portal shall provide a natural, complementary extension to the Metasys site management UI, as described in this section.

Ready Access Portal Architecture:  Implement to conform to industry standards, so that it may accommodate the required applications provided as well as communicate information to and from the Metasys system site director.

PC Hardware:  The PC(s) shall be configured as follows:

Memory:  2 GB, 1 GB Minimum.

CPU Pentium 4 processor.  2.8 Hz clock speed, 2.0 GHz minimum.

Hard Drive:  200 GB free hard drive space, 80 GB minimum.

Hard Drive Backup System:  CD/RW, DVD/RW or network backup software provided by IT department.

DVD ROM Drive:  16X performance.

Ports:  1 Serial and 2 USB ports.

Keyboard:  101 keyboard and 2-button mouse.

CRT configuration.

17-inch flat panel monitor, 1280 x 1024 resolution minimum.

16 bit or higher color resolution.

LAN Communications:  Ethernet communications board, 100 Mbps minimum.

Operating System Software:

Windows 7 or 8 Professional, IIS Version 5.1, .Net Version 2.0, SQL server 2005 express software with SP2 or Microsoft Windows Server 2003 OS with SP2, IIS Version 6.0, .Net version 2.0 and SQL Server 2005 with SP2.

Provide software and hardware required for integration of computing hardware on enterprise IT network.

Provide software registration cards for all included software.

UI Application Components:

The ready access portal shall provide an intuitive UI to key Metasys functions and tasks via web browser.

Plug-ins or special software shall not be required for access to alarm, summary, schedule, or trend data.

The portal shall include the ability to view full graphical representations of systems and equipment on PC platforms.

The control system shall provide secure sockets level and active directory service support. If the active directory service and single sign-on features are enabled and the user is logged in to the Windows desktop, access to the system shall be automatic and the login screen shall not appear.

Provide a common tool for graphics creation, schedule creation, custom programming, user access, and hardware definition.

Information shall be accessible on both PC and handheld device platforms as follows:

PCs.  Internet Explorer Version 7.0, recommended.

Handheld Devices.  Internet Explorer for Window Mobile Version 5.0 or 6.0, recommended, as well as Apple i-Phone, i-Touch, or i-Pad.  UI shall be optimized for devices with a 240x320 pixel screen size (QVGA).

Operator Interface:

Password access shall be as described in this section for management portal UI.

Once logged in, the system shall display a pre-selected screen tailored to the task requirements of the individual user.

The UI shall utilize an intuitive navigation and display method designed for operators accessing the system for casual information and control or on an infrequent basis.  It shall feature three basic components:

Radio buttons for selecting the type of information to be displayed including alerts, summary, schedules, and diagnostics.

Navigation tree for selection of the specific data to be displayed on screen for the selected type.  The navigation tree may be hidden and expanded by the operator to optimize the display of information.

A display window that provides the selected information by type in a pre-configured tabular format.

The UI software shall provide help menus and instructions for each operation and/or application.

The system shall provide support for up to 100 concurrent users from an unlimited universe individuals with defined password access to the system.

The system shall utilize secure sockets level support as required to allow the ready access portal to communicate across a network in a way designed to prevent eavesdropping, tampering, and message forgery. It provides endpoint authentication and communications privacy over the network using cryptography.

The system shall have the capability to display multiple navigation trees that correspond to the user views configured in the management portal UI.

The alert summary of the ready access portal shall, at the minimum, provide the following information:

Alert or alarm type.

Date and time of alert occurrence.

Priority color coded to level.

Item name.

Item value, if applicable.

Message.

Any attribute of any object in the system may be designated to report an alarm.

A standard summary on the ready access portal shall, at minimum, provide the following information:

Point type graphic icon.

Item name.

Item value.

Item status.

Access to the change value window, if applicable, for the purpose of setting, holding, or releasing an item value.

A custom summary on the ready access portal shall display user-specified summaries of key data sets that can be quickly filtered and sorted.  Items within these custom summaries may be commanded.

A graphic view on the ready access portal shall display, as describe in this section for management portal UI.

The schedule detail summary of the ready access portal shall, at minimum, provide the following information:

Scheduled occurrences including time and value.

Scheduled overrides including start time, end time, and value.

A list of all scheduled items including name and attribute, value, status, and priority.

Access to the “add temporary override” window for the purpose of adding a temporary override to the schedule.

The diagnostic (trend) summary of the ready access portal, as viewed on a personal computing device, shall provide the following information:

Item name.

Item status.

Trend name.

Trend status.

Full path name.

Access to a detailed summary including trended value, time, and date arranged in a user-selectable format of 1, 12, 24, 48, or 72 hours.

FMS Architecture:

The FMS shall use an open architecture and fully support a multi-vendor environment.  To accomplish this effectively, the FMS shall support open communication protocol standards and integrate a wide variety of third-party devices and applications.  The system shall be designed for use on the Internet, or intranets using “off the shelf,” industry standard technology compatible with other Port-provided networks.

The FMS system shall consist of the following:

Standalone NAE.

Field equipment controller(s).

Input/output module(s) (IOM).

Local display device(s).

Portable operator's terminal(s).

Distributed UI(s).

Network processing, data storage, and communications equipment.

Other components required for a complete and working FMS.

The system shall be modular in nature, and shall permit expansion of both capacity and functionality through the addition of sensors, actuators, controllers, and operator devices, while reusing existing controls equipment.

System architectural design shall eliminate dependence upon any single device for alarm reporting and control execution.  The failure of any single component or network connection shall not interrupt the execution of control strategies at other operational devices.

Automation Network:

The automation network shall be based on a PC industry standard of Ethernet TCP/IP.  Where used, LAN controller cards shall be standard “off-the-shelf” products available through normal PC vendor channels.

The FMS shall network multiple UI clients, automation engines, system controllers, and ASC.  Provide application and data server(s) as required for systems operation.

The automation network shall be capable of operating at a communication speed of 100 Mbps, with full peer-to-peer network communication.

NAE shall reside on the automation network.

The automation network shall be compatible with other enterprise-wide networks.  Where indicated, the automation network shall be connected to the enterprise network and share resources with it by way of standard networking devices and practices.

Control Network:

NAE shall provide supervisory control over the control network.

BACnet Protocol Integration, BACnet.

The neutral protocol used between systems shall be BACnet over Ethernet and comply with the ASHRAE BACnet standard 135-2008.

A complete PICS shall be provided for all BACnet system devices.

Provide the ability to command, share point object data, COS data and schedules between the host and BACnet systems.

Environmental Conditions:  The DDC panels and all other field equipment shall be rated for continuous operation under ambient environmental conditions of 35ºF to 120ºF dry bulb and 10 percent to 95 percent relative humidity, noncondensing.  Instrumentation and control elements shall be rated for continuous operation under the ambient environmental temperature, pressure, humidity, and vibration conditions specified or normally encountered for the installation.

System Accuracy and Display:

The DDC system shall control space temperature with a range of 50ºF to 85ºF ±1ºF for conditioned space (display to nearest 0.5ºF); 30ºF to 130º ±1ºF for unconditioned space (display to nearest 0.5ºF).  Return air humidity shall be controlled to 20 percent RH to 35 percent RH ±3 percent RH.

The DDC system shall control duct temperature with a range of 40ºF to 140ºF ±1ºF (display to nearest 0.5ºF).

Water temperature shall be displayed with a range of 30ºF to 100ºF ±1ºF (display to nearest 0.5ºF); the range of 100ºF to 300ºF ±2ºF (display to nearest 0.5ºF); and water temperatures for the purpose of performing BTU calculations using differential temperatures to ±0.5ºF using matched sensors (display to nearest 0.5ºF).

Pressure shall be displayed with a range for the specific application ±5 percent of range.

Airflow or differential airflow shall be displayed with a range for the specific application of ±4 percent of range (display to nearest 1.0 CFM).

MATERIALS AND EQUIPMENT

Controls and Power Wiring:

General:  Electric equipment and wiring shall be in accordance with Division 26.  Manual or automatic control and protective or signal devices required for operation specified, and any control wiring required for controls and devices, shall be provided hereunder.  Run all control wiring in conduit.

Wiring:

Field and Subfield Panels:  Voltage in panels shall not exceed 120 volts.  Where devices are wired to higher voltages, mount in suitable individual enclosures or group in separate control panel.  Coordinate electrical power supply with Division 26.  Provide conduit and wiring required to spare breakers in accordance with Division 26.

Motor Control Centers:  Ensure correct voltage of holding coils and starter wiring in pre-wired motor control centers to interface with automatic controls.

Wiring for the primary peer-to-peer communications network shall be two conductor minimum 18-gauge foil-shielded, stranded twisted pair cable rated at 100 Vdc or more at 80ºC.

Cable types shall be of a different color coding for easy identification and troubleshooting.  Recommended color coding:

Analog Input Cable – Yellow

Analog Output Cable – Tan

Binary Input Cable	– Orange

Binary Output Cable – Violet

24 Vac Cable – Gray

General Purpose Cable	 – Natural

Wiring for secondary network shall be three-conductor minimum 22-gauge telephone type wire.  If LON works communications are used, provide two-conductor cable.

Communications Links Surge Protection:  Protect all communications equipment against surges induced on communications link.  All cables and conductors which serve as communications links shall have surge protection circuits installed that meet the requirements of REA PE-60d.

Communications Links Overvoltage Protection:  Protect communications equipment against overvoltage on communications link conductors.  Cables and conductors which serve as communications links shall have overvoltage protection for voltages up to 480 VAC rms, 60 Hz installed.  Instrument fuses or fusible resistors will be accepted for this application.

Control Panels:

Wall-mounted control panels shall be provided as required to contain all relays, terminal strips, power supplies and other equipment in the building control system.

Panels shall be UL listed, minimum NEMA 1, minimum 14-gauge steel with stiffeners, continuous hinge doors, locking handles, single point latch.  Alternately, panels may be constructed of structural plastic meeting UL and NEMA requirements.

CONTROL DEVICES

Input:

Temperature Instruments:

Room Temperature Sensors:  Platinum or nickel RTD type with accuracy of ±0.5ºF at 70ºF; operating range 50 to 90ºF; linear to DDC system; single point sensing element in wall-mounted ventilated enclosure with insulating back plate or ceiling pendant mount.  Acceptable manufacturers are JCI, Veris, or pre-bid approved equal.  Combination temperature, humidity, and/or carbon dioxide sensors may be used.  Sensors shall have:

No digital readout display.

User adjustment based on DDC programmed offset.

A room occupancy sensor installed as shown on the drawings.

Wireless capability as shown on the drawings.

Duct Temperature Sensors:  Platinum or nickel RTD element with accuracy of ±0.5ºF at 65ºF, averaging type consisting of array of single point sensing elements, securely mounted in duct or plenum; operating range 30 to 100ºF; linear signal; 20-foot element.

Outside Air Temperature Sensor:  Platinum or nickel RTD element with accuracy of ±0.5ºF at 32ºF; Range -50 to 250ºF, single element, linear, with weather and sun shield for exterior mounting.

Low Temperature Limit Thermostat:  Minimum 1-foot capillary sensing element for 1 square foot of air flow area, triggering on low temperature as sensed by any 6-inch segment; snap acting, normally open contacts, manual reset, line voltage.

Liquid Immersion Temperature Sensor:  Platinum or nickel RTD element, with accuracy of ±0.65ºF at 70ºF, stainless steel well and assembly, range -50 to 220ºF.

Humidity Instruments:

Space Humidity Sensors:  Operating range 10 to 95 percent relative humidity, accuracy ±5%, surface mounted ventilated enclosure for wall mounting,  Acceptable manufacturers are JCI, Veris, or pre-bid approved equal.  Combination temperature, humidity, and/or carbon dioxide sensors may be used.  Sensors shall have:

No digital readout display.

No user adjustment based on DDC programmed offset.

Wireless capability as shown on the drawings.

Duct Humidity Transmitter:  Capacitive type sensor and transmitter, linear output signal, automatic temperature compensating, air filter, ±2% RH accuracy from 0 to 100% RH, industrial quality.

Occupancy Sensors:  Sensors shall have a manual override button and wireless capability.  Acceptable Manufacturers:  Johnson WRZ, or pre-bid approved equal.

Airflow Measuring Station (Fan Inlet):

Acceptable Manufacturers:  Ebtron, Air Monitor, Paragon, Johnson, or pre-bid approved equal.

Electronic air measuring system consisting of thermistor based sensor probe assemblies and a single microprocessor based transmitter.  Each sensor probe assembly shall contain one or more independently wired sensor housings.  The airflow and temperature readings calculated for each sensor housing shall be equally weighted and averaged by the transmitter prior to output.

Fan inlet airflow traverse probe with two bead-in-glass thermistor probes, mounted on 304 stainless steel blocks and feet with adjustable mounting rods.

Microprocessor and Electronics:  Solid state microprocessor, permanent non-volatile memory, regulated power supply, software-based system.  0-5 Vdc, 0-10 Vdc, or 4-20 mA signals, linear flow and temperature outputs, line surge, and transient protection.

Performance:  ±2 percent of reading, +20 FPM across total calibrated range of 0 to 5,000 FPM, for duct mounted, 0-10,000 FPM for fan inlet mounted repeatability better than ±0.4 percent of reading.  Pressure drop shall not exceed 0.005 in. WG at 2000 FPM.

Probes shall be capable of producing steady, non-pulsating signals of standard total and static pressure, without need for flow corrections or factors with an accuracy of 3 percent of actual flow over a fan operating range of 6 to 1 capacity turndown.

Air Flow Station (Duct-Mounted):

Acceptable Manufacturers:  Ebtron, Kurz, Johnson, or pre-bid approved equal.

Electronic air measuring system consisting of thermistor based sensor grid and microprocessor based electronics.

Sensor Probes:  Thermistors probes and linear IC’s, aluminum casing, duct-mounted, wiring Teflon or kynar coated and encased, 20°F to 160°F operating range, weather resistant finish, flanged welded aluminum frame.

Microprocessor and Electronics:  Solid state microprocessor, permanent non-volatile memory, regulated power supply, software based system, 0-5 Vdc, 0-10 Vdc, or 4-20 mA signals, linear flow and temperature outputs, line surge and transient protection.

Performance:  ±2 percent, +20 FPM across total calibrated range of 0 to 5000 FPM, for duct mounted, 0-10,000 FPM for fan inlet mounted, repeatability better than ±0.4 percent of reading.  Pressure drop shall not exceed 0.005 inches W.G. at 2000 FPM.

Airflow Transmitters:  Provide transmitter with 4-20 mA output signal, 16 character alpha-numeric display capable of displaying airflow, temperature, system status, configuration setting, and diagnostics.  Pressure transducers accurate to + 0.25 percent for full range, range selected based on the actual flow element and expected velocity pressure, and linear output on velocity turndown of 10 to 1.  Acceptable manufacturers are Ebtron GTA 116, Setra Model C264, or pre-bid approved equal.  Provide a calibration certificate for each unit.

Air Differential Pressure Switch:  Required for filter status.  Setpoint shall be adjustable with operating range of 0.05 to 5 inches W.G.  Contactor shall close when set pressure differential is met or exceeded.

Air Duct Static Pressure Transmitter:  Operating range 0 to 5 inches WC for duct-mounted transmitter and 0 to 12 inches WC for fan high limit transmitters.  Sensors shall be diaphragm or rigid element bellows, electronic type.  Each transmitter shall be provided with stop cock, and tubing for attaching portable pressure gauge.  Sensing tube shall be securely mounted in duct with appropriate fitting.

Damper Position Indication:  Where called for in the sequence of operations or on the drawings, provide a means of indicating damper position.  Where two-position electric direct-coupled actuators are used, provide two auxiliary switches with SPDT contacts to indicate the fully open or fully closed positions as required.  Where pneumatic or other types of actuators are used, provide an encapsulated mercury switch mated to a damper crank arm, which can be mounted on the damper control shaft to indicate the open or closed position.

Leak Detection:

Provide addressable water leak detection system that utilizes water sensing cable to detect the presence of water at any point along its length.

Detection cable shall each be 40 feet minimum in length and consist of two parallel conductors with a supervised end of line resistor circuit.  The conductors shall be individually insulated with a protective outer covering of braided rayon.

Leak detection shall interface with the DDC system.

Duct-Mounted Carbon Dioxide Sensors:  Self-sufficient CO2 sampling station with pump to ensure proper air flow to sensing chamber.  Solid state sensor, accuracy of ±2 percent of span, maximum span of 0-2500 ppm.  Provide single calibration kit with calibration gas, connecting hoses, and fittings.  Acceptable manufacturers are Vulcain, Veris, Johnson Controls, or pre-bid approved equal.

Wall-Mounted Carbon Dioxide Sensors:  Infrared sensing, microprocessor controlled digital transmitting carbon dioxide gas monitor suitable for wall mounting.  Sensors shall be hard wired, unless drawings indicate sensor to be wireless.  Combination temperature, humidity, and/or carbon dioxide sensors may be used.

| Detection Range: | 0-2000 ppm, 0-2% or 0-5% |
| --- | --- |
| Accuracy: | +/- 13% |
| Response Time: | <60 seconds (for 90% of the reading) |
| Outputs: | 4-20mA (optional: SPDT Relay rated 5A) |
| Relay Output Rating: | 5A, 30 Vdc or 250 Vac (resistive load) |
| Power Requirement: | 17-27 Vac or 24-38 Vdc, 200 mA |
| Operating Temperature Range: | 32°F to 100°F (0°C to 40°C) |
| Operating Humidity Range: | 0% - 95% RH, Non-Condensing |
| Display: | Sensor shall not be provided with digital display. |
| Acceptable Manufacturers: | Vulcain Series, Veris, Johnson Controls, or pre-bid approved equal. |

Oxygen Detector:  Diffusion fuel cell sensing oxygen gas monitor to be used in a network configuration.

| Detection Range: | 0-1 PPM |
| --- | --- |
| Accuracy: | +/- 3% |
| Outputs: | 4-20mA, 0-5 Vdc or 0-10 Vdc |
| Relay Output Rating: | 5A, 30 Vdc or 250 Vac (resistive load) |
| Power Requirements: | 17-27 Vac, 24-38 Vdc, 250 mA |
| Operating Temperature Range: | -4°F to 131°F (-20 to 55°C) |
| Operating Humidity Range: | 5% - 95% RH, Non-condensing |
| Display: | Sensor shall be provided with digital display. |
| Acceptable Manufacturers: | Vulcain VA201TQ1 Series, Veris, Johnson Controls, or pre-bid approved equal. |

Basic Water Flow Meters:  Provide insertion electromagnetic flow meter and BTU meter that provides analog output signals to the DDC system.

| Accuracy: | +/- 1% of reading from 0.25-20 ft/sec |
| --- | --- |
| Liquid Temperature Range: | 15-300°F |
| Maximum Operating Pressure: | 400 psi |
| Output Signal: | Analog 4-20mA signal |
| Acceptable Manufacturers: | Onicon F-3500 with system-10 BTU meter, or pre-bid approved equal. |

Water Flow Meters:  Provide flange by flange electromagnetic flow meter and BTU meter that provides analog output signals to the DDC system.

| Accuracy: | +/- 1% of reading from 0.25-20 ft/sec |
| --- | --- |
| Liquid Temperature Range: | 15-300°F |
| Maximum Operating Pressure: | 400 psi |
| Output Signal: | Analog 4-20mA signal |
| Acceptable Manufacturers: | Onicon F-4000 with system, or pre-bid approved equal. |

Water Differential Pressure Transmitter:  4-20 mA proportional output signal, with provisions for field checking.  Sensors shall withstand up to 150 percent of rated pressure without damaging the device, and shall be accurate to within ± 0.25 percent from 20 percent above and below normal operating range of sensed variable.  Sensors shall include a nulling valve assembly.  Setra, Verus, Yokogawa, or pre-bid approved equal.

Current Sensing Switches:

The current sensing switch shall be self-powered with solid state circuitry and a dry contact output.  It shall consist of a current transformer, a solid state current sensing circuit, adjustable trip point, solid state switch, SPDT relay, and an LED indicating the on or off status.  A conductor of the load shall be passed through the window of the device.  It shall accept over-current up to twice its trip point range.

Current sensing switches shall be used for run status for fans, pumps, and other miscellaneous motor loads.

Current sensing switches shall be calibrated to show a positive run status only when the motor is operating under load.  A motor running with a broken belt or coupling shall indicate a negative run status.

Acceptable manufacturers:  Veris Industries or pre-bid approved equal.

Air Pressure Safety Switches:

Air pressure safety switches shall be of the manual reset type with SPDT contacts rated for 2 amps at 120 Vac.

Pressure range shall be adjustable with appropriate scale range and differential adjustment for intended service.

Acceptable Manufacturers:  Johnson Controls, Cleveland Controls, Dwyer, or pre-bid approved equal.

Output:

Motorized control valves, pressure independent type, for use in variable flow heating and chilled water systems:

Acceptable Manufacturers:  Flow Control, Inc. Delta P Valve, or pre-bid approved equal.

Description:

Pressure independent control valves shall be dynamic, modulating two-way, control device for use in variable flow chilled water and heating water systems.

Dynamic control valve shall accurately control flow, independent of system pressure fluctuation, from 0 to 100 percent full rated flow.

Test ports shall be furnished with valve.

Valve Actuator:

Valve actuator shall be factory-mounted and calibrated to provide full design flow at end of stroke and 100 percent control signal.

Actuator shall accept 2-10 Vdc, 4-20mA or 3-point floating electric signal and shall include resistor to facilitate any of these signals.

Actuator shall be capable of providing 4-20mA or 2-10 Vdc feedback signal to the control system.

Actuator shall be capable of control between maximum and minimum signal.  End stroke of actuator at full design shall be factory set at design flow indicated on the drawings from performance curves furnished with valves.  For example, 100 percent control signal would control 100 percent design flow, 50 percent signal would control 50 percent design flow.

Actuators shall power valve to either open or closed position from any position in case of power failure.

External LED read-out of current valve position and maximum valve position setting shall be available.

Provide current limiting for stalled actuators.

Actuators shall be sized to provide the required close off torque and be able to open/close a valve in 200 seconds or less.

Valve Body:

Valves 1/2 inch to 2 inches shall be constructed of brass, rated at 150 psi working pressure.

Valves 3 inches and greater shall be constructed of ductile iron, rated at 150 psi working pressure.

Flow Regulation Unit:  Flow regulation unit shall be capable of controlling flow within ±5 percent of rated flow, due to system pressure fluctuations.

Motorized control valves, pressure dependent type, for use in constant flow heating systems:  Equip with modulating plug or V-port inner valve with composition disc for tight shutoff.  Two-position valves shall be line size, modulating water valves shall be sized at 3 psi drop or as shown on the drawings.  Screwed ends except 2 1/2-inch and larger valves with flanged ends.  Select valves to modulate smoothly at all system pressures and flows.  Select valves with close-off ratings and spring ranges designed to operate at the maximum flows and maximum available pump heads scheduled without leakage or spring range shift.  Bubble tight butterfly valves acceptable on 2 1/2-inch lines and above for two-position action only.  Use pressure dependent, two position, motorized valves for controlling water flow to cabinet unit heaters and unit heaters in variable flow heating water systems.

Electronic Valve and Damper Operators:

Electronic modulating type with low voltage DC or current positioning signal or low voltage AC motive power.

Each actuator shall have current limiting circuitry incorporated in its design to prevent damage to the actuator.

Modulating and two-position actuators shall be provided as required by the sequence of operations.  Actuators shall provide the minimum torque required for proper valve close-off against the system pressure for the required application.  The valve actuator size shall be based on the valve manufacturer’s recommendations for flow and pressure differential.  The spring return feature shall permit normally open or normally closed positions of the valves, as required.  All direct shaft mount rotational actuators shall have external adjustable stops to limit the travel in either direction.

Modulating actuators shall accept 24 VAC or Vdc power supply and be UL listed.  The control signal shall be 2-10 Vdc or 4-20 mA.  Where required by sequence, the actuator shall provide a clamp position feedback signal of 2-10 Vdc.  The feedback signal shall be independent of the input signal, and may be used to parallel other actuators and provide true position indication.  The feedback signal of each valve actuator (except terminal valves) shall be wired back to a terminal strip in the control panel for troubleshooting purposes.  Use 120 Vac as shown on the drawings.

Two-position or open/closed actuators shall accept 24 Vac power supply and be UL listed.  Butterfly isolation and other valves, as specified in the sequence of operations, shall be furnished with adjustable end switches to indicate open/closed position or be hard wired to start/stop the associated pump or chiller.  Use 120 Vac as shown on the drawings.

N2 DDC FIELD PANELS

Use BACnet controllers toggled to N2.  See the BACnet Field Panels article in this section.

BACNET FIELD PANELS

DDC System Controllers:  Advanced Application Field Equipment Controller (FAC):

Completely user-programmable and digital controllable that communicates via BACnet MS/TP protocol or optionally via N2Open.

Supports BACnet Standard MS/TP Bus Protocol ASHRAE SSPC-135, Clause 9 on the controller network.

The FAC shall be BTL certified and carry the BTL Label.

The FAC shall be tested and certified as a BACnet ASC.

Provide a BACnet PICS.

Provide a finite state control engine to eliminate unnecessary conflicts between control functions at crossover points in their operational sequences.  Submittals for non-state-based DDC shall provide separate control strategy diagrams for all controlled functions.

Controllers shall be factory programmed with a continuous adaptive tuning algorithm that senses changes in the physical environment and continually adjusts loop tuning parameters appropriately.  Controllers that require manual tuning of loops or perform automatic tuning on command only will not be acceptable.

Assemble in a plenum-rated plastic housing with flammability rated to UL94-5VB.

Include an integral real-time clock and support time-based tasks which enables these field controllers to monitor and control the following:

Schedules.

Calendars.

Alarms.

Trends.

Continue time-based monitoring when offline for extended periods of time from a Metasys system network.

Operate as a stand-alone controller in applications that do not require a networked supervisory device or for network applications where it is preferred to have the scheduling, alarming, and/or trending performed locally in the field controllers.

Include troubleshooting LED indicators to identify the following conditions:

Power on.

Power off.

Download or startup in progress, not read for normal operation.

No faults.

Device fault.

Field controller bus – normal data transmission.

Field controller bus – no data transmission.

Field controller bus – no communication.

Sensor actuator bus – normal data transmission.

Sensor actuator bus – no data transmission.

Sensor actuator bus – no communication.

Accommodate the direct wiring of analog and binary I/O field points.

Supports the following types of inputs and outputs:

Universal inputs shall be configured to monitor any of the following:

Analog Input, Voltage Mode.

Analog Input, Current Mode.

Analog Input, Resistive Mode.

Binary Input, Dry Contact Maintained Mode.

Binary Input, Pulse-Counter Mode.

Binary inputs shall be configured to monitor dry-contact maintained mode or pulse counter mode.

Analog outputs shall be configured to monitor analog output, voltage mode or analog output, current mode.

Binary outputs shall output line-voltage relay outputs and 24 Vac Triac.

Configurable outputs shall be capable of analog output, voltage mode and binary output mode.

Ability to reside on a field controller bus (FC bus).

The FC bus shall be a MS/TP bus supporting BACnet Standard protocol SSPC-135, Clause 9.

The FC bus shall support communications between the FAC and the NAE.

The FC bus shall support a minimum of 100 IOMs and FACs, in any combination.

The FC bus shall operate at a maximum distance of 15,000 feet between the FACs and the farthest connected drive.

Ability to monitor and control a network of sensors and actuators over a sensor actuator Bus (SA bus).

The SA bus shall be a MS/TP bus supporting BACnet Standard Protocol SSPC-135, Clause 9.

The SA bus shall support a minimum of 10 devices per trunk.

The SA bus shall operate at a maximum distance of 1,200 feet between the FAC and the farthest connected device.

Capability to execute complex control sequences involving direct wired I/O points as well as input and output devices communicating over the FC bus or the SA bus.

Supports the following applications:

Chilled water/central plant optimization applications, including but not limited to:

Selection and sequencing of no more than eight chillers of different sizes.

Selection and sequencing of no more than eight (each) primary and secondary chilled water pumps of varying pumping capacities.

Selection and sequencing of no more than eight condenser water pumps.

Selection and sequencing of cooling towers and bypass valve including single speed, multi-speed, and vernier control.

Selection and sequencing of no more than four heat exchangers of different capacities.

A proven and documented central cooling plant optimization program that incorporates custom equipment efficiency profiles, without rewriting software code, in order to meet the building load using the least amount of energy as calculated.

The use of advanced control algorithms that apply equipment specific parameters, including operational limits and efficiency profiles in order to determine equipment start and runtime preferences.

Identification of the most efficient equipment combination and automatic control of state and speed of all necessary equipment to balance runtime, optimize timing, and sequencing and ensure the efficiency and stability of the central cooling plant.

Control definition for the chiller plant in a FAC or network control engine (NCE), as supported by available memory and point I/O, or capable of being split across multiple FACs, FECs, or NCEs.

Heating central plant applications.

Built-up air handling units for special applications.

Terminal and package units.

Special programs as required for systems control.

Supports a local controller display (DIS-1710) either as an integral part of the FAC or as a remote device communicating over the SA bus.

The display shall use a BACnet Standard SSPC-135, Clause 9 MS/TP protocol.

The display shall allow the user to view monitored points without logging into the system.

The display shall allow the user to view and change setpoints, modes of operation, and parameters.

The display shall provide password protection with user adjustable password timeout.

The display shall be menu driven with separate paths for I/O, parameter/setpoint, and overrides.

The display shall use easy-to-read English text messages.

The display shall allow the user to select the points to be shown and in what order.

The display shall support a back lit liquid crystal display (LCD) with adjustable contrast and brightens and automatic backlight brightening during user interaction.

The display shall be a minimum of four lines and a minimum of 20 characters per line.

The display shall have a keypad with no more than six keys.

The display shall be panel mountable.

DDC System Controllers:  Field Equipment Controller (FEC):

Fully user-programmable, digital controller that communicates via BACnet MS/TP protocol.

Provide a finite state control engine to eliminate unnecessary conflicts between control functions at crossover points in their operational sequences.  Submittals for non-state-based DDC shall provide separate control strategy diagrams for all controlled functions.

Controllers shall be factory programmed with a continuous adaptive tuning algorithm that senses changes in the physical environment and continually adjusts loop tuning parameters appropriately.  Controllers that require manual tuning of loops or perform automatic tuning on command only will not be acceptable.

Include a removable base to allow pre-wiring without the controller.

Assemble in a plenum-rated plastic housing with flammability rated to UL94-5VB.

Include troubleshooting LED indicators to identify the following conditions:

Power on.

Power off.

Download or startup in progress, not read for normal operation.

No faults.

Device fault.

Field controller bus – normal data transmission.

Field controller bus – no data transmission.

Field controller bus – no communication.

Sensor actuator bus – normal data transmission.

Sensor actuator bus – no data transmission.

Sensor actuator bus – no communication.

Accommodate the direct wiring of analog and binary I/O field points.

Supports the following types of inputs and outputs:

Universal inputs shall be configured to monitor any of the following:

Analog Input, Voltage Mode.

Analog Input, Current Mode.

Analog Input, Resistive Mode.

Binary Input, Dry Contact Maintained Mode.

Binary Input, Pulse-Counter Mode.

Binary inputs shall be configured to monitor dry-contact maintained mode or pulse counter mode.

Analog outputs shall be configured to monitor analog output, voltage mode or analog output, current mode.

Binary outputs shall output line-voltage relay outputs and 24 Vac Triac.

Configurable outputs shall be capable of analog output, voltage mode and binary output mode.

Ability to reside on a field controller bus (FC bus).

The FC bus shall be a MS/TP bus supporting BACnet Standard protocol SSPC-135, Clause 9.

The FC bus shall support communications between the FEC and the NAE.

The FC bus shall support a minimum of 100 IOMs and FECs, in any combination.

The FC bus shall operate at a maximum distance of 15,000 feet between the FACs and the farthest connected drive.

Ability to monitor and control a network of sensors and actuators over a sensor actuator bus (SA bus).

The SA bus shall be a MS/TP bus supporting BACnet Standard Protocol SSPC-135, Clause 9.

The SA bus shall support a minimum of 10 devices per trunk.

The SA bus shall operate at a maximum distance of 1,200 feet between the FAC and the farthest connected device.

Capability to execute complex control sequences involving direct-wired I/O points as well as I/O devices communicating over the FC bus or the SA bus.

Supports, but is not limited to, the following:

Hot water, chilled water/central plant applications.

Built-up air handling units for special applications.

Terminal units.

Special programs as required for systems control.

Field Devices:

IOM:

Additional inputs and outputs for use in the FEC.

Communicate with the FEC over either the FC bus or the SA bus using BACnet Standard protocol SSPC-135, Clause 9.

Assembled in a plenum-rated plastic housing with flammability rated to UL94-5VB.

Four points, minimum, to 17 points, maximum.

Support the following types of inputs and outputs:

Universal inputs shall be configured to monitor any of the following:

Analog Input, Voltage Mode.

Analog Input, Current Mode.

Analog Input, Resistive Mode.

Binary Input, Dry Contact Maintained Mode.

Binary Input, Pulse-Counter Mode.

Binary inputs shall be configured to monitor dry-contact maintained mode or pulse counter mode.

Analog outputs shall be configured to monitor analog output, voltage mode or analog output, current mode.

Binary outputs shall output line-voltage relay outputs and 24 Vac Triac.

Configurable outputs shall be capable of analog output, voltage mode and binary output mode.

Include troubleshooting LED indicators to identify the following conditions:

Power on.

Power off.

Download or startup in progress, not read for normal operation.

No faults.

Device fault.

Normal data transmission.

No data transmission.

No communication.

Networked Thermostat (TEC 26X6 and TEC 26X5):

Be capable of controlling a four-pipe for TEC 26X6 or a two-pipe for TEC 26X5, fan coil system with multi-speed fan control.

Communicate over the FC bus using BACnet Standard protocol SSPC-135, Clause 9.

Support remote read/write and parameter adjustment from the web-based UI through an NAE.

Include an intuitive UI providing plain text messages:

Two line, 8 character backlit display.

LED indicators for fan, heat, and cool statuses.

5 UI keys:

Mode.

Fan.

Override.

Degrees C/F.

Up/Down.

The display shall continuously scroll through the following parameters:

Room temperature.

System mode.

Schedule Status:  Occupied/Unoccupied/Override.

Applicable alarms.

Provide the flexibility to support any one of the following inputs:

Integral indoor air temperature sensor.

Duct mount air temperature sensor.

Remote indoor air temperature sensor with occupancy override and LED indicator.

Two configurable binary inputs.

Minimum of six levels of keypad lockout.

Provide flexibility to adjust the following parameters:

Adjustable temporary occupancy, from 0 to 24 hours.

Adjustable heating/cooling deadband, from 2º F to 5º F.

Adjustable heating/cooling cycles per hour, from 4 to 8.

Include nonvolatile, electrically erasable, programmable read-only memory for all adjustable parameters.

TEC 26X5 shall provide the flexibility to support either of the following outputs:

One fan control.

One proportional (0 to 10V).

VAV Modular Assembly (VMA):

Provide both standalone and networked DDC of pressure-independent, variable air volume terminal units.  It shall address both single and dual duct applications.

Capable of communicating over the FC bus using BACnet Standard protocol SSPC-135, Clause 9.

Internal electrical isolation for AC power, DC inputs, and MS/TP communications.  An externally mounted isolation transformer will not be acceptable.

Configurable digital controller with integral differential pressure transducer and damper actuator.  All components shall be connected and mounted as a single assembly that can be removed as one piece.

Assembled in a plenum-rated plastic housing with flammability rated to UL94-5VB.

The integral damper actuator shall be a fast response stepper motor capable of stroking 90 degrees in 30 seconds for quick damper positioning to speed commissioning and troubleshooting tasks.

The controller shall determine airflow by dynamic pressure measurement using an integral dead-ended differential pressure transducer.  The transducer shall be maintenance-free and shall not require air filters.

Each controller shall have the ability to automatically calibrate the flow sensor to eliminate pressure transducer offset error due to ambient temperature/humidity effects.

The controller shall utilize a proportional plus integration algorithm for the space temperature control loops.

Each controller shall continuously, adaptively tune the control algorithms to improve control and controller reliability through reduced actuator duty cycle.  In addition, this tuning reduces commissioning costs and eliminates the maintenance costs of manually re-tuning loops to compensate for seasonal or other load changes.

The controller shall provide the ability to download and upload VMA configuration files, both locally and via the communications network.  Controllers shall be able to be loaded individually or as a group using a zone schedule generated spreadsheet of controller parameters.

Control setpoint changes initiated over the network shall be written to VMA non-volatile memory to prevent loss of setpoint changes and to provide consistent operation in the event of communication failure.

The controller firmware shall be flash-upgradeable remotely via the communications bus to minimize costs of feature enhancements.

The controller shall provide fail-soft operation if the airflow signal becomes unreliable, by automatically reverting to a pressure-dependent control mode.

The controller shall interface with balancer tools that allow automatic recalculation of box flow pickup gain (“K” factor), and the ability to directly command the airflow control loop to the box minimum and maximum airflow setpoints.

Controller performance shall be self-documenting via on-board diagnostics.  These diagnostics shall consist of control loop performance measurements executing at each control loop’s sample interval, which may be used to continuously monitor and document system performance.  The VMA shall calculate exponentially weighted moving averages for each of the following.  These metrics shall be available to the end user for efficient management of the VAV terminals.

Absolute temperature loop error.

Signed temperature loop error.

Absolute airflow loop error.

Signed airflow loop error.

Average damper actuator duty cycle.

The controller shall detect system error conditions to assist in managing the VAV zones.  The error conditions shall consist of:

Unreliable space temperature sensor.

Unreliable differential pressure sensor.

Starved box.

Actuator stall.

Insufficient cooling.

Insufficient heating.

The controller shall provide a flow test function to view damper position versus flow in a graphical format.  The information would alert the user to check damper position.  The VMA would also provide a method to calculate actuator duty cycle as an indicator of damper actuator runtime.

The controller shall provide a compliant interface for ASHRAE Standard 62 and shall be capable of resetting the box minimum airflow based on the percent of outdoor air in the primary air stream.

The controller shall comply with ASHRAE Standard 90.1 by preventing simultaneous heating and cooling, and where the control strategy requires reset of airflow while in reheat, by modulating the box reheat device fully open prior to increasing the airflow in the heating sequence.

Inputs:

Analog inputs with user-defined ranges shall monitor the following analog signals, without the addition of equipment outside the terminal controller cabinet:

0-10 Vdc sensors.

1000 ohm RTDs.

NTC thermistors.

Binary inputs shall monitor dry contact closures.  Inputs shall provide filtering to eliminate false signals resulting from input “bouncing.”

For noise immunity, inputs shall be internally isolated from power, communications, and output circuits.

Provide side loop application for humidity control.

Outputs:

Analog outputs shall provide 0-10 Vdc control outputs.

Binary outputs shall provide a SPST Triac output rated for 500mA at 24 Vac.

Configure VMA with a software tool that provides a simple question/answer format for developing applications and downloading.

The VMA shall support the following sensors:

Communicate over the SA bus with a network sensor.

LCD display room sensor.

Standard room sensors as defined by analog input requirements.

Humidity sensors defined by the analog inputs side loop.

Network Sensors:

Ability to monitor the following variables as required by the systems sequence of operations.

Zone temperature.

Zone humidity.

Zone setpoint.

Transmit the zone information back to the controller on the SA bus using BACnet Standard protocol SSPC-135, Clause 9.

Include the following items as shown on the drawings:

A backlit LCD to indicate the temperature, humidity and setpoint.

An LED to indicate the status of the override feature.

A button to toggle the temperature display between Fahrenheit and Celsius.

A button to initiate a timed override command.

Available with either screw terminals or phone jack.

Available in either surface mount or wall mount styles.

UPS PRODUCT SPECIFICATIONS

General:  Provide an uninterruptable power supply (UPS) for the network control modules (NCMs) and fire/smoke dampers as specified below.  The UPS shall be fed by 120V AC emergency power circuits.  The UPS shall be floor or wall mountable.

UPS for Fire/Smoke Dampers:  Provide MGE Pulsar UPS, or pre-bid approved equal.  Products shall carry UL 1778 listing.  Base sizing on inrush current requirements of connected actuators and include 15 percent factor of safety.  Connect input to emergency power circuit panel.  Connect output to FSD control circuit.  Provide manufacturer’s standard three-year comprehensive warranty, including batteries.

UPS for NAEs:  Provide Functional Devices PSH550-UPS, or pre-bid approved equal.  Products shall carry UL 1778 listing.  Base sizing on peak current requirements of connected NAE and include 15 percent factor of safety.  Connect input to emergency power circuit panel.  Connect output to NAE.  Provide manufacturer’s standard three-year comprehensive warranty, including batteries.

NETWORK AUTOMATION ENGINES (NAE 35/45/55XX)

The NAE shall be a fully user-programmable, supervisory controller.  The NAE shall monitor the network of distributed application-specific controllers, provide global strategy and direction, and communicate on a peer-to-peer basis with other NAE.

The NCE shall include a minimum of 33 I/O points.

Network:  Reside on the automation network and support a sub-network of system controllers.

User Interface :  Each NAE shall have the ability to deliver a web-based UI as described in this section.  All computers connected physically or virtually to the automation network shall have access to the web-based UI.

The web-based UI software shall be imbedded in the NAE.  Systems that require a local copy of the system database on the user’s PC will not be acceptable.

The NAE shall support a maximum of four concurrent users.

The web-based user shall have capability to access all system data through one NAE.  Remote users connected to the network through an Internet Service Provider or telephone dial up shall also have total system access through one NAE.

Systems that require the user to address more than one NAE to access all system information will not be acceptable.

The NAE shall have the capability of generating web based UI graphics.  The graphics capability shall be imbedded in the controller.

Systems that support UI graphics from a central database or require the graphics to reside on the user’s PC will not be acceptable.

The web based UI shall support the following functions using a standard version of Microsoft Internet Explorer:

Configuration.

Commissioning.

Data Archiving.

Monitoring.

Commanding.

System Diagnostics.

Systems that require workstation software or modified web browsers will not be acceptable.

The NAE shall allow temporary use of portable devices without interrupting the normal operation of permanently connected modems.

Processor:  Microprocessor-based with a minimum word size of 32 bits, multi-tasking, multi-user, and real-time digital control processors.  Use standard operating systems.  NAE size and capability shall be sufficient to fully meet the requirements of these specifications.

Memory:  Each NAE shall have sufficient memory to support its own operating system, databases, and control programs, and to provide supervisory control for all control level devices.

Hardware Real-Time Clock:  An integrated, hardware-based, real-time clock.

Include troubleshooting LED indicators to identify the following conditions:

Power:  On/Off.

Ethernet Traffic:  Ethernet traffic/no Ethernet traffic.

Ethernet Connection Speed:  10 Mbps/100 Mbps.

FC Bus A:  Normal communications/no field communications.

FC Bus B:  Normal communications/no field communications, NAE55 only.

Peer Communication:  Data traffic between control devices.

Run:  Control running/control in startup/control shutting down/software not running.

Battery Fault:  Battery defective, data protection battery not installed.

24 Vac:  Present/Loss of 24 Vac.

Fault:  General fault.

Include paragraphs k and l only if modem is being provided, otherwise delete.

Modem RX:  Modem receiving data.

Modem TX:  Modem transmitting.

Communications Ports:  Provide ports for operation of operator I/O devices, such as industry-standard computers, modems, and portable operator’s terminals.

USB Port:  2.

URS-232 Serial Data Communication Port:  2.

RS-485 Port: 2.

Ethernet Port:  1.

Diagnostics:  Continuously perform self-diagnostics, communication diagnosis, and diagnosis of all panel components.  The NAE shall provide both local and remote annunciation of any detected component failure, low battery conditions, or repeated failures to establish communication.

Power Failure:  In the event of the loss of normal power, the NAE shall continue to operate for a user adjustable period for a maximum of 10 minutes, after which there shall be an orderly shutdown of all controllers to prevent the loss of database or operating system software.

During a loss of normal power, the control sequences shall go to the normal system shutdown conditions.  All critical configuration data shall be saved into flash memory.

Upon restoration of normal power and after a minimum off-time delay, the NAE shall automatically resume full operation without manual intervention through a normal soft-start sequence.

Certification:  The NAE shall be UL listed.

Controller Network:  Support the following communication protocols on the controller network simultaneously:

Support BACnet Standard MS/TP Bus Protocol ASHRAE SSPC-135, Clause 9 on the controller network:

A BACnet PICS shall be provided for each controller device (master or slave) that will communicate on the BACnet MS/TP bus.

Control Devices:

NAE35, 50 devices, maximum.

NAE45, 100 devices, maximum.

NAE55, 200 devices, maximum.

Support LonWorks-enabled devices using the FTT-10.  All LonWorks controls devices shall be LonMark-certified.

Support the Johnson Controls N2 Field Bus.

Conform to EIA Standard RS-485.

Include a master/slave protocol where the controller is the master.

Include a four level priority system for polling frequency.

Optically isolated from the controller.

Supports the Metasys Integrator System.

NETWORK INTEGRATION ENGINES (NIE 29/39/49/59XX)

The NIE shall be a fully user-programmable, supervisory controller.  The NIE shall monitor the network of distributed application-specific controllers, provide global strategy and direction, and communicate on a peer-to-peer basis with other NIE.

Network:  Reside on the automation network and shall support a sub-network of system controllers.

User Interface:  Each NIE shall have the ability to deliver a web-based UI as described in this section.  All computers connected physically or virtually to the automation network shall have access to the web-based UI.

The web-based UI software shall be imbedded in the controllers.  Systems that require a local copy of the system database on the user’s PC will not be acceptable.

Support a maximum of four concurrent users.

The web-based user shall have capability to access all system data through one NIE controller.  Remote users connected to the network through an Internet Service Provider or telephone dial up shall also have total system access through one NIE.

Systems that require the user to address more than one NIE to access all system information will not be acceptable.

The NIE shall have the capability of generating web based UI graphics.  The graphics capability shall be imbedded in the controller.

Systems that support UI graphics from a central database or require the graphics to reside on the user’s PC will not be acceptable.

The web based UI shall support the following functions using a standard version of Microsoft Internet Explorer:

Configuration.

Commissioning.

Data archiving.

Monitoring.

Commanding.

System diagnostics.

Systems that require workstation software or modified web browsers will not be acceptable.

The NIE shall allow temporary use of portable devices without interrupting the normal operation of permanently connected modems.

Processor:  Microprocessor-based with a minimum word size of 32 bits, multi-tasking, multi-user, and real-time digital control processors.  Use standard operating systems.  NIE size and capability shall be sufficient to fully meet the requirements of these specifications.

Memory:  Each NIE shall have sufficient memory to support its own operating system, databases, and control programs, and to provide supervisory control for all control level devices.

Hardware Real-Time Clock:  An integrated, hardware-based, real-time clock.

Include troubleshooting LED indicators to identify the following conditions:

Power:  On/Off.

Ethernet Traffic:  Ethernet traffic/no Ethernet traffic.

Ethernet Connection Speed:  10 Mbps/100 Mbps.

FC Bus A:  Normal communications/no field communications.

FC Bus B:  Normal communications/no field communications, NIE59 only.

Peer Communication:  Data traffic between control devices.

Run:  Control running/control in startup/control shutting down/software not running.

Battery Fault:  Battery defective, data protection battery not installed.

24 Vac:  Present/Loss of 24 Vac.

Fault:  General fault.

Include paragraphs k and l only if modem is being provided, otherwise delete.

Modem RX:  Modem receiving data.

Modem TX:  Modem transmitting.

Communications Ports:  Provide ports for operation of operator I/O devices, such as industry-standard computers, modems, and portable operator’s terminals.

USB Port:  2.

URS-232 Serial Data Communication Port:  2.

RS-485 Port: 2.

Ethernet Port:  1.

Diagnostics:  Continuously perform self-diagnostics, communication diagnosis, and diagnosis of all panel components.  The NIE shall provide both local and remote annunciation of any detected component failure, low battery conditions, or repeated failures to establish communication.

Power Failure:  In the event of the loss of normal power, the NIE shall continue to operate for a user adjustable period for a maximum of 10 minutes, after which there shall be an orderly shutdown of all controllers to prevent the loss of database or operating system software.

During a loss of normal power, the control sequences shall go to the normal system shutdown conditions.  All critical configuration data shall be saved into flash memory.

Upon restoration of normal power and after a minimum off-time delay, the controller shall automatically resume full operation without manual intervention through a normal soft-start sequence.

Certification:  The NIE shall be UL listed.

Controller Network:  Support the following communication protocols on the controller network simultaneously:

Support BACnet Standard MS/TP Bus Protocol ASHRAE SSPC-135, Clause 9 on the controller network:

A BACnet PICS shall be provided for each controller device (master or slave) that will communicate on the BACnet MS/TP bus.

Control Devices:

NIE29, 32 devices, maximum.

NIE39, 50 devices, maximum.

NIE49, 100 devices, maximum.

NIE59, 200 devices, maximum.

Support LonWorks-enabled devices using the FTT-10.  All LonWorks controls devices shall be LonMark-certified.

Support the Johnson Controls N2 Field Bus.

Conform to EIA Standard RS-485.

Include a master/slave protocol where the controller is the master.

Include a four level priority system for polling frequency.

Optically isolated from the controller.

Supports the Metasys Integrator System.

NIE for Third-Party Device and Equipment:  NIEx9 supervisory engines may integrate power and energy meters, lighting, HVAC, security, access control, and many proprietary systems that communicate over Modbus, M-Bus (EN1434-3) and KNX Bus.

NIEx9s shall leverage standard building management communication technologies, including:

BACnet® Protocol:  The NIEx9 supports the BACnet services and objects typically used by a workstation and a field controller device including BACnet alarm, scheduling, trend, and event services.

MS/TP FC Bus:  The BACnet MS/TP FC bus is a standard peer-to-peer, multiple-master protocol in which each master device takes turns originating messages to pass to any device on the bus.

LonWorks® protocol:  Specified NIEx9 models can supervise LonWorks devices if the network interface follows current LonMark guidelines and uses FTT-10.

N2 Bus Protocol:  The N2 bus is an open Johnson Controls field communications trunk that links ASC and programmable controllers to a supervisory controller.

Modbus®:  NIEx9 supports both Modbus RTU (RS-485, RS-232) and Modbus TCP/IP connectivity.

Meter Bus (M-Bus):  M-Bus is a European standard (EN 1434-3) that applies to heat meters.

KONNEX (KNX) Protocol:  KNX bus is used to control lighting, blinds and shutters, heating, and attendance systems.  KNX was created from the European Installation Bus, BatiBUS, and European Home System protocols.  A KNX IP Gateway is required to connect a NIEx9 to a KNX network.

NETWORK CONTROL ENGINES (NCE 25XX)

The NCE shall be a fully user-programmable, supervisory controller.  The NCE shall monitor the network of distributed application-specific controllers, provide global strategy and direction, and communicate on a peer-to-peer basis with other NCE.

Include a minimum of 33 I/O points.

Network:  Reside on the automation network and shall support a sub-network of system controllers and support a subnet of 32 field controllers.

User Interface:  Each NCE shall have the ability to deliver a web-based UI as described in this section.  All computers connected physically or virtually to the automation network shall have access to the web-based UI.

The web-based UI software shall be imbedded in the controllers.  Systems that require a local copy of the system database on the user’s PC will not be acceptable.

Support a minimum of two concurrent users.

The web-based user shall have capability to access all system data through one NCE controller.  Remote users connected to the network through an Internet Service Provider or telephone dial up shall also have total system access through one NCE.

Systems that require the user to address more than one NCE to access all system information will not be acceptable.

The NCE shall have the capability of generating web based UI graphics.  The graphics capability shall be imbedded in the controller.

Systems that support UI graphics from a central database or require the graphics to reside on the user’s PC will not be acceptable.

The web based UI shall support the following functions using a standard version of Microsoft Internet Explorer:

Configuration.

Commissioning.

Data archiving.

Monitoring.

Commanding.

System diagnostics.

Systems that require workstation software or modified web browsers will not be acceptable.

The NCE shall allow temporary use of portable devices without interrupting the normal operation of permanently connected modems.

Processor:  Microprocessor-based with a minimum word size of 32 bits, multi-tasking, multi-user, and real-time digital control processors.  Use standard operating systems.

Memory:  Each NCE shall have sufficient memory to support its own operating system, databases, and control programs, and to provide supervisory control for all control level devices.

Hardware Real-Time Clock:  An integrated, hardware-based, real-time clock.

Include troubleshooting LED indicators to identify the following conditions:

Power:  On/Off.

Ethernet Traffic:  Ethernet traffic/no Ethernet traffic.

Ethernet Connection Speed:  10 Mbps/100 Mbps.

FC Bus:  Normal communications/no field communications.

SA Bus:  Normal communications/no field communications.

Peer Communication:  Data traffic between control devices.

Run:  Control running/control in startup/control shutting down/software not running.

Battery Fault:  Battery defective, data protection battery not installed.

Fault:  General fault.

10 LNK.

100 LNK.

Include paragraphs k and l only if modem is being provided, otherwise delete.

Modem RX:  Modem receiving data.

Modem TX:  Modem transmitting.

Communications Ports:  Provide ports for operation of operator I/O devices, such as industry-standard computers, modems, and portable operator’s terminals.

USB Port:  1.

URS-232 Serial Data Communication Port:  1.

RS-485 Port: 1.

RJ-45 Ethernet Port:  1.

Jack:  1.

Diagnostics:  Continuously perform self-diagnostics, communication diagnosis, and diagnosis of all panel components.  Provide both local and remote annunciation of any detected component failure, low battery conditions, or repeated failures to establish communication.

Power Failure:  In the event of the loss of normal power, the NCE shall continue to operate for a user adjustable period for a maximum of 10 minutes, after which there shall be an orderly shutdown of all controllers to prevent the loss of database or operating system software.

During a loss of normal power, the control sequences shall go to the normal system shutdown conditions.  All critical configuration data shall be saved into flash memory.

Upon restoration of normal power and after a minimum off-time delay, the controller shall automatically resume full operation without manual intervention through a normal soft-start sequence.

Certification:  The NCE shall be UL listed and file E107041, CCN PAZX, UL 916, Energy Management Equipment and be FCC compliant to CFR47, Part 15, Subpart B, Class A.

Controller Network:  Support the following communication protocols on the controller network simultaneously:

Support BACnet Standard MS/TP Bus Protocol ASHRAE SSPC-135, Clause 9 on the controller network:

A BACnet PICS shall be provided for each controller device (master or slave) that will communicate on the BACnet MS/TP bus.

Control Devices:  NCE:  32 devices, minimum.

Support LonWorks-enabled devices using the FTT-10.  All LonWorks controls devices shall be LonMark-certified.

Support the Johnson Controls N2 Field Bus.

Conform to EIA Standard RS-485.

Include a master/slave protocol where the controller is the master.

Include a four level priority system for polling frequency.

Optically isolated from the controller.

Supports the Metasys Integrator System.

Ability to monitor and control a network of sensors and actuators over an SA bus and to execute complex control sequences involving direct wired I/O points as well as input and output devices communicating over the field trunk or the SA bus:

MS/TP bus supporting BACnet Standard protocol SSPC-135, Clause 9.

Support 10 devices, minimum.

Operate at a maximum distance of 1,200 feet between the NCE and the farthest connected device.

Employ a finite state control engine to eliminate unnecessary conflicts between control functions at crossover points in their operational sequences.  Non-state based DDC shall submit separate control strategy diagrams for all controlled functions.

Factory-programmed with a continuous adaptive tuning algorithm that senses changes in the physical environment and continually adjusts loop tuning parameters appropriately.  Controllers that require manual tuning of loops or perform automatic tuning on command only will not be acceptable.

Assembled in a plenum-rated plastic housing with flammability rated to UL94-5VB.

Employ an industrial single-board computer.

Employ nonvolatile flash memory to store all programs and data and a data protection battery to save data and power the real time clock when primary power is interrupted.

Provide removable, color coded, screw terminal blocks for 24 Vac power, communication bus, and I/O point field wiring.

Support an optional internal modem with RJ-12 6-pin telephone line connector.

Support a Local Controller Display (DIS-1710) either as an integral part of the NCE or as a remote device communicating over the SA bus.

Use a BACnet Standard SSPC-135, clause 9 MS/TP protocol.

Allow the user to view monitored points without logging into the system.

Allow the user to view and change setpoints, modes of operation, and parameters.

Provide password protection with user adjustable password timeout.

Menu driven with separate paths for:

Input/Ouput.

Parameter/Setpoint.

Overrides.

Use easy-to-read English text messages.

Allow the user to select the points to be shown and in what order.

Support a backlit LCD with adjustable contrast and brightens and automatic backlight brightening during user interaction.

4 lines, minimum, and 20 characters per line, minimum.

Keypad with 6 keys, maximum.

Panel mountable.

Support the following number and types of inputs and outputs:

Ten Universal Inputs:

Analog input, voltage mode.

Analog input, current mode.

Analog input, resistive mode.

Binary input, dry contact maintained mode.

Binary input, pulse counter mode.

Eight Binary Inputs:

Dry contact maintained mode.

Pulse Counter mode.

Seven Binary Outputs:

24 Vac Triac.

Four Analog Outputs:

Analog output, voltage mode.

Analog input, current mode.

Four Configurable Outputs:

Analog output, voltage mode.

Binary output, 24 Vac Triac mode.

Support the following applications:

Central equipment including chillers and boilers.

Lighting and electrical distribution.

Built-up air handling units for special applications.

Power generation and energy monitoring equipment.

Interfaces to security and fire detection systems.

WIRELESS FIELD BUS SYSTEM, ZFR1800 SERIES

The ZFR1800 series system shall employ ZigBee technology to create a wireless mesh network to provide wireless connectivity for Metasys BACnet devices at multiple system levels.  This includes communications from FEC and VMA field controllers to sensors and from engines to these field controllers.  Wireless devices shall coexist on the same network with hardwired devices.  Hardwired controllers shall be capable of retrofit to wireless devices with no special software.

The ZFR1810 wireless field bus coordinator shall provide a wireless interface between supported field controllers and an NAE35/45/55 or NCE25 supervisory controller via the BACnet MS/TP field bus.  Each wireless mesh network shall be provided with a ZFR1810 coordinator for initiation and formation of the network.

The ZFR1811 wireless field bus router shall be used with any model FEC or VMA1600 series VMA to provide a wireless interface to supervisory engines via the ZFR1810 coordinator and associated WRZ wireless mesh room temperature sensors.

ZFR coordinators and routers shall meet the following requirements:

Use direct sequence spread spectrum radio frequency (RF) technology.

Operate on the 2.4 GHZ ISM band.

Meet the IEEE 802.15.4 standard for low-power, low duty-cycle RF transmitting systems.

FCC compliant to CFR Part 15 Subpart B, Class A.

ZFR coordinators shall operate as a bidirectional transceiver with the sensors and routers to confirm and synchronize data transmission and shall be capable of communication with sensors and routers up to a maximum distance of 250 feet (line of sight).

ZFR routers shall operate as a bidirectional transceiver with other mesh network devices to ensure network integrity and be capable of communication with other mesh network devices at a maximum distance of 250 feet (line of sight).

ZFR coordinators and routers shall be assembled in a plenum rated plastic housing with flammability rated to UL94-5VB.

ZFR coordinators and routers shall include LED indicators to provide diagnostic information required for efficient operation, troubleshooting, and commissioning.

ONE-TO-ONE WIRELESS ROOM TEMPERATURE SENSOR SYSTEM, WRZ SERIES

The WRZ-TT series wireless room temperature sensors shall sense and transmit room temperatures, room set point, room occupancy notification, and low battery condition to an associated ZFR1811 router and the WRZ receiver.

The One-To-One Wireless Receiver (WRZ Receiver) shall receive wireless RF signals containing temperature data from multiple WRZ sensors and communicate this information to either FEC or VMA controllers via the SA bus.

Sensors and receivers shall meet the following requirements:

Use direct sequence spread spectrum RF technology.

Operate on the 2.4 GHZ ISM band.

Meet the IEEE 802.15.4 standard for low-power, low duty-cycle RF transmitting systems.

FCC compliant to CFR Part 15 Subpart B, Class A.

Assembled in NEMA 1 plastic housing.

WRZ sensors shall be available with:

Warmer/cooler set point adjustment.

No set point adjustment.

Set point adjustment scale, 55º F to 85º F.

Wireless refrigerator/freezer temperature transmitter, for ZFR receiver only.

NIST rated wireless refrigerator/freezer temperature transmitter, for ZFR receiver only.

WRZ receivers shall operate as a bidirectional transceiver with the sensors to confirm and synchronize data transmission.

WRZ receivers shall be capable of communication with one to five WRZ sensors, to a distance of 200 feet, maximum.

WRZ sensors shall include a display for room temperature, signal strength, fan mode, and occupancy and network statuses, as required by application and shown in the contract documents.

WRZ receivers shall have LED indicators to provide information for the following:

Power.

SA Bus:  Receiver activity/no activity.

Wireless RF:  Transmission from sensors/no transmission.

Wireless Rapid Transmit Mode:  No transmission/weak signal/adequate signal/excellent signal.

SYSTEM TOOLS

The system configuration tool (SCT) shall be a software package enabling a computer platform to be used as a stand-alone engineering configuration tool for an NAE or an NIE and shall provide an archive database for the configuration and application data.

Include the following features:

Same look and feel at the UI regardless of whether the configuration is being done online or offline.

Basic system navigation tree for connected networks.

Integration of Metasys N1, LonWorks, and BACnet enabled devices.

Customized user navigation trees.

Point naming operating parameter setting.

Graphic diagram configuration.

Alarm and event message routing.

Graphical logic connector tool for custom programming.

Downloading, uploading, and archiving databases.

The SCT shall have the capability to automatically discover field devices on connected buses and networks.  Automatic discovery shall be available for the following field devices:

BACnet devices.

LonWorks devices.

N2 bus devices.

Metasys N1 networks.

The SCT shall be capable of programming the FECs and field devices by meeting the following requirements:

Capability to configure, simulate, and commission.

Allow the FECs and field devices to be run in simulation mode to verify the applications.

Contain a library of standard applications to be used for configuration.

A wireless access point shall allow a wireless enabled portable PC to make a temporary Ethernet connection to the automation network.

The wireless connection shall allow the PC to access the SCT through the web browser using the UI.

The wireless use of SCT shall be the same as a wired connection in every respect.

The wireless connection shall use the Bluetooth Wireless Technology.

Wireless MS/TP Converter:

Provide a temporary wireless connection between the SA or FC bus and a wireless enabled portable PC.

Support downloading and troubleshooting FEC and field devices from the PC over the wireless connection.

Include Bluetooth Wireless Technology.

Power through a connection to either the SA or FC bus.

Operate over a minimum of 33 feet within a building.

Comply with FCC Part 15.247 regulations for low-power unlicensed transmitters.

Include LED indicators to provide the following information:

Power:  On/Off

Fault:  Fault/No Fault

SA/FC Bus:  Bus Activity/No Bus Activity

Bluetooth:  Bluetooth Communication Established/Bluetooth Communication Not Established.

Handheld VAV Balancing Sensor (ATV7003):

The sensor shall be a light weight portable device of dimensions not more than 3.2 x 3.2 x 1.0 inches.

Capable of displaying data and setting balancing parameters for VAV control applications.

Powered through a connection to either the SA or FC bus.

Menu-driven device that shall modify itself automatically depending upon what type of application resides in the controller.

Contain a dial and two buttons to navigate through the menu and to set balancing parameters.

Provide an adjustable time-out parameter that returns the controller to normal operation if the balancing operation is aborted or abandoned.

The sensor shall be UL 916 listed and CSA certified C22.2 N. 205, CFR47

The sensor shall include the following:

5-foot retractable cable.

Laminated user guide.

Nylon carrying case.

LOCAL CONTROL PANELS

Add requirements for panel louvers and/or keyed locks to the paragraph below if these options are included in the project.

All control panels shall be factory constructed, incorporating the FMS manufacturer’s standard designs and layouts.  All control panels shall be UL inspected and listed, as an assembly, and carry a UL 508 label listing compliance.  Control panels shall be fully enclosed with perforated sub-panel, hinged door, and slotted flush latch.

General:  The control panels shall consist of the DDC controller(s), display module as shown on the drawings, and I/O devices such as relays, transducers, etc., that are not required to be located external to the control panel due to function.  The display module shall be flush mounted in the panel face where specified.

All I/O connections on the DDC controller shall be provide via removable or fixed screw terminals.

Low and line voltage wiring shall be segregated.  All provided terminal strips and wiring shall be UL listed, 300-volt service, and provide adequate clearance for field wiring.  All wiring shall be neatly installed in plastic trays or tie-wrapped.

Provide a 120 volt convenience outlet, fused on/off power switch, and required transformers in each enclosure.

DC power supplies shall be sized for the connected device load.  Total rated load shall not exceed 75 percent of the rated capacity of the power supply.  An appropriately sized fuse and fuse block shall be provided and located next to the power supply.  A power disconnect switch shall be provided next to the power supply.

Input:  120 Vac +10%, 60Hz.

Output: 24 Vdc.

Line Regulation: +0.05% for 10% line change.

Load Regulation: +0.05% for 50% load change.

Ripple and Noise: 1 mV rms, 5 mV peak to peak.

INPUT/OUTPUT (I/O) FUNCTIONS

Analog Inputs (AI):  The AI function shall monitor each analog input, perform A-to-D conversion, and hold the digital value in a buffer for interrogation.  Provide signal conditioning for each analog input.  Individually calibrate all analog inputs for zero and span, in hardware or in software.

Analog Outputs (AO):  The AO function shall accept digital data, perform D-to-A conversion, and output a signal compatible with the operator.  Individually calibrate all analog outputs for zero and span.  Provide short circuit protection.

Digital Inputs (DI):  The DI function shall accept on/off, open/close, or other COS (two-state data) indications.  Provide isolation and protection against input voltage up to 180 Vac peak.

Digital Outputs (DO):  The DO function shall provide contact closures for momentary and maintained operation of output devices.  Closures shall have a minimum duration of 0.1 second.

EXECUTION

INSTALLATION PRACTICES

Mounting Panels:  Locate panels where shown on the drawings or near item of equipment to be controlled, but not on equipment itself.

DDC Field Panels:  Locations shown on the drawings are recommended locations and do not indicate actual quantity or location.  Provide number of panels required to accommodate all DI, DO, AI, and AO points and all hardware and software to accomplish specified control sequences.  Locate all panels in mechanical or electrical rooms.  Submit proposed locations for approval prior to preparing control drawings.

Electrical:

Provide control wiring for all control devices and control panels.

Provide power wiring for all control devices and control panels.  Obtain power from spare circuits in emergency power panels.

All wiring, including low voltage wiring, shall be installed in minimum 3/4-inch conduit in mechanical rooms or other locations susceptible to damage.  Plenum rated cable shall be used in other locations.

Grounding:  Instrumentation and communication grounding shall be installed as necessary to preclude ground loops, noise, and surges from adversely affecting system operation.

Control voltage shall be limited to a maximum of 120 volts.

Where relay coil is connected to load side of motor starter to energize with motor operation, external control circuit shall be properly fused with fuse block located in respective starter enclosure.

Where relays are used to control single phase motors directly, provide contacts rated for not less than horsepower rating of largest motor switched by relay.

UPS:  Provide UPS systems to power all NCM panels.  Provide UPS systems to power all combination fire/smoke dampers.

Identification:  Provide engraved nameplates identifying all switches, lights and starters, and each control device where control function is not readily apparent.

Room Sensors:  Mount at height of 4 feet for wall-mounted sensor and thermostats with adjustment on face.  Mount at height of 5 feet for all wall-mounted thermostats and sensors which do not have adjustment face.  Provide insulating back on thermostats mounted on exterior walls.  Provide one sensor for each zone of temperature control.

Carbon Dioxide Sensors and Oxygen Detectors:

Mount at 5 feet above finished floor, or as shown on the drawings.

Provide quantity as required by coverage rating (20-foot radius, maximum), or as shown on the drawings.

Carbon dioxide sensor shall alarm above 850 PPM.

Oxygen detector operating system to maintain 19.5 percent.  Alarm if levels exceed 23 percent for longer than 15 minutes.

See Sequence of Operations Article in this section for more information.

Airflow Station (Duct-Mounted):  Install grid array in ductwork where shown.  Provide gasket between frame and duct.  Mount electronic components in nearest temperature control panel.  Install in accordance with the manufacturer’s instructions.

Airflow Station (Fan Inlet):  Install in fan inlet bell in accordance with the manufacturer’s instructions.

Water Flow Meters:  Install devices in accordance with the manufacturer’s recommendations, with sufficient upstream and downstream straight pipe to obtain accurate readings.

SEQUENCES OF OPERATION

All controls shall be accomplished by the DDC control system, unless otherwise noted.

Typical of large central AHU serving mezzanine, enplaning, and deplaning levels of terminal and concessions.

Custom variable air volume, air handling units with supply and return fans and outside air intake:

Occupied Cycle:

The supply and return fans shall run continuously.

The minimum outside air airflow measuring station shall signal the DDC controller which shall modulate the normally closed minimum outside air damper, normally open return damper, and normally closed relief damper to maintain the required minimum outside air quantity (adjustable).  Carbon dioxide sensors located as shown on the drawings shall signal the DDC controller which resets the required minimum outside air quantity (adjustable) when the carbon dioxide level in the return air exceeds the maximum acceptable value of 1000 PPM (adjustable).  When the minimum outside air CFM has reached its maximum value and the carbon dioxide level in the return air exceeds the maximum acceptable value, the DDC controller shall reset the air terminal unit minimum CFM settings to the high minimum CFM values.  The minimum outside air CFM shall be a variable which shall be calculated by adding the respective CFM values (adjustable) for each exhaust fan serving that air handling system at any point in time, plus a constant CFM value (adjustable) for building pressurization.  Obtain actual CFM values from the air balancer.  Refer to air flow diagram for building pressurization CFM.

A discharge air temperature sensor shall signal the DDC controller which shall modulate in sequence the normally closed main outside air and normally closed relief air dampers, the normally open return air damper, the normally open heating coil valve, and the normally closed cooling coil valve to maintain a 55ºF (adjustable) discharge air temperature.  The discharge air temperature setpoint shall be reset to 65ºF (adjustable) when the outside air temperature is below 40ºF (adjustable).  Discharge air temperature reset shall be accomplished using a linear schedule starting at 40ºF, with full reset occurring at 30ºF outside air temperature (adjustable).

Outside air, return air and mixed air temperature sensors shall signal the DDC controller.  The main outside air damper and relief damper shall be closed when the outside air temperature exceeds the return air temperature.

A discharge air plenum static pressure sensor shall signal the DDC controller which shall signal the variable speed controller to control the supply fan to maintain the required discharge static pressure (adjustable).  All system air terminal units shall signal the DDC controller which shall reset the discharge air static pressure setpoint to the value that maintains at least one terminal unit control damper in the wide open position while still satisfying the zone temperature setpoint.

Duct static pressure sensors shall signal the DDC controller.

Airflow measuring stations located at the supply and return fan shall signal the DDC controller which shall signal the variable speed controller to control the return fan to maintain the required return air CFM according to the following equation:

Return Air CFM = 	Supply Air CFM

minus	Exhaust Air CFM

minus	Building Pressurization CFM

If the return fan reaches a minimum speed (adjustable) and the equation is not satisfied, the DDC controller shall override normal return air damper control and modulate the damper to satisfy the above equation.  DDC controller shall receive rpm signal from each variable speed controller.  The exhaust air CFM shall be a variable in the above equation which shall be calculated by adding the respective CFM values (adjustable) for each exhaust fan in operation at any point in time.  Obtain actual exhaust fan CFM values from the air balancer.

Shutdown Mode:

When an air handling unit is not in operation, the following conditions shall exist:

The supply and return fans shall not operate.

All dampers and valves shall be in their normal de-energized positions, except for the return dampers, which shall be closed.

All combination fire/smoke dampers shall be closed.

Startup Mode:

Allow ample time for the return dampers to open before starting the fans.

The return fan shall start ahead of the supply fan.

Alarms/Safeties:

A smoke detector located in the supply air shall signal the DDC controller, which shall initiate the shutdown mode upon detection of smoke in the airstream.  An alarm shall be generated.

A low limit detection thermostat located between the heating and cooling coils shall signal the DDC controller, which shall initiate the shutdown mode upon sensing a temperature below 40ºF (adjustable).  An alarm shall be generated.

A differential pressure switch located across the filter bank shall signal the DDC controller, which shall generate an alarm when the static pressure drop exceeds 0.75 inches W.G. (adjustable).

A discharge air plenum static pressure sensor shall signal the DDC controller which shall override the supply fan speed control algorithm to limit the static pressure to a maximum of 3 inches W.G. (adjustable).  If the static pressure exceeds 3.5 inches W.G. (adjustable), the DDC controller shall initiate the shutdown mode and generate an alarm.  A manual reset, discharge air plenum static pressure switch shall be hard-wired to shut down the supply fan in the event that the static pressure exceeds 3.75 inches W.G. (adjustable).

A manual reset static pressure switch located in the mixing plenum shall be hardwired to shut down the supply fan in the event that the static pressure exceeds -2.0 inches W.G. (adjustable).

A manual reset static pressure switch located in the return fan inlet shall be hardwired to shut down the return fan in the event that the static pressure exceeds -2.0 inches W.G. (adjustable).

Each variable speed controller shall signal the DDC controller in the event of drive/control failure.  An alarm shall be generated.

Provide safety interlocks to position the return dampers to their normal de-energized positions when the associated supply or return fans are started.

A signal from the fire alarm panel shall signal the DDC controller to initiate the shutdown mode and close the combination fire/smoke dampers in the supply and return ductwork.

Typical of AHU serving south terminal lobby and concourse retail/concession nodes.

Single zone variable volume air handling units with supply and return air (or relief/exhaust) fans and outside air intake:

Occupied Cycle:

The following air handling units shall operate in tandem (from a common signal):  AHU-x-xxx and x-xxx together.

The supply fan shall run continuously.

The normally closed minimum outside air damper shall be open.

A discharge air temperature sensor shall signal the DDC controller, which shall modulate the normally closed cooling control valve and the supply fan variable speed controller to maintain the required discharge air temperature setpoint.  The supply fan shall modulate between design and minimum air flow (65 percent maximum design, adjustable) to maintain the required discharge air temperature.  
At minimum air flow the DDC controller shall modulate the normally closed main outside air and normally open return air dampers to maintain discharge air temperature.  If the air flow has reached its scheduled minimum and the discharge temperature remains below setpoint, the normally closed hot water coil valve shall be modulated and the air flow increased to maintain the required discharge temperature setpoint.  The discharge air temperature setpoint shall be reset based on averaging a total of two temperature sensors.

Outside air and return air temperature sensors shall signal the DDC controller.  The outside air damper and relief damper shall return to their minimum positions when the outside air temperature exceeds the return air temperature.

Air flow measuring stations located in the supply and return fans (or return air duct upstream of relief exhaust fan) shall signal the DDC controller, which shall signal the variable speed controller to control the return fan (or relief exhaust fans) to maintain the required return (or relief) air CFM according to the following equation:

Return (Relief/Exhaust) Air CFM = 	Supply Air CFM

minus	Exhaust Air CFM

minus	Building Pressurization CFM

If the return (or relief) fan reaches a minimum speed (adjustable) and the equation is not satisfied, the DDC controller shall override normal return air damper control and modulate the damper to satisfy the above equation.  DDC controller shall receive rpm signal from each variable speed controller.  Exhaust air CFM shall be a variable in the above equation which shall be calculated by adding the respective CFM values (adjustable) for each associated exhaust fan (other than relief/exhaust) in operation at any point in time.  Obtain actual exhaust fan CFM values from the air balancer.

A mixed air temperature sensor shall signal the DDC controller.

Static pressure sensor in mixing box shall signal controller which shall limit maximum percent open position of main outdoor air damper and return damper to maintain negative 0.15-inches W.G. (adjustable) in mixing box.

Shutdown Mode:

When an air handling unit is not in operation, the following conditions shall exist:

The supply and exhaust fans shall not operate.

All dampers and valves shall be in their normal de-energized positions.

All combination fire/smoke dampers shall be closed.

Startup Mode:  Allow ample time for the relief and return dampers to open before starting the fans.

Alarms/Safeties:

A smoke detector located in the supply air shall signal the DDC controller, which shall initiate the shutdown mode upon detection of smoke in the airstream.  An alarm shall be generated.

A low limit detection thermostat located between the heating and cooling coils shall signal the DDC controller, which shall initiate the shutdown mode upon sensing a temperature below 40ºF (adjustable).  An alarm shall be generated.

A differential pressure switch located across the filter bank shall signal the DDC controller, which shall generate an alarm when the static pressure drop exceeds 0.75 inches W.G. (adjustable).

Current transformers located in the supply and return (or relief exhaust) fan power circuits shall signal the DDC controller and generate an alarm in the event of fan/control failure.

Provide safety interlocks to position the return dampers to their normal de-energized positions when the associated supply and return (or relief exhaust) fans are started.

A signal from the fire alarm panel shall signal the DDC controller to initiate the shutdown mode and close the combination fire/smoke dampers in the supply and return ductwork.

A manual reset static pressure switch located in the mixing plenum shall be hard-wired to shut down the supply fan and return (or relief exhaust) fan in the event that the static pressure exceeds -2.0 inches W.G. (adjustable).

Typical of AHU serving utility tunnels.

Air handling unit 100 percent outside air, constant volume with heating coil and face and bypass dampers:

Occupied Cycle:

The supply fan shall run continuously.

The normally closed outside air damper shall be open.

A discharge air temperature sensor shall signal the DDC controller, which shall modulate the normally open heating coil valve to maintain a 60ºF (adjustable) discharge air temperature.

When the outside air temperature is below 40ºF (adjustable), the DDC controller shall open the heating coil valve wide and modulate the normally open face and normally closed bypass dampers to maintain a 60ºF (adjustable) discharge air temperature.

Shutdown Mode:

When the air handling unit is not in operation, the following conditions shall exist:

The supply fan shall not operate.

All dampers and valves shall be in their normal, de-energized positions.

All combination fire/smoke dampers shall be closed.

Alarms/Safeties:

A smoke detector located in the supply air duct shall signal the DDC controller, which shall initiate the shutdown mode upon detection of smoke in the airstream.  An alarm shall be generated.

A low limit detection thermostat located downstream of the heating coil shall signal the DDC controller, which shall initiate the shutdown mode upon sensing a temperature below 40ºF (adjustable).  An alarm shall be generated.

A differential pressure switch located across the filter bank shall signal the DDC controller, which shall generate an alarm when the static pressure drop exceeds 0.5 inches W.G. (adjustable).

A current transformer located in the supply fan power circuit shall signal the DDC controller, which shall generate an alarm in the event of fan/control failure.

A signal from the fire alarm panel shall signal the DDC controller to initiate the shutdown mode and close the combination fire/smoke dampers in the supply ductwork.

Variable Air Volume Terminal Unit:  Space temperature sensor shall signal the DDC controller, which shall modulate air damper between maximum cooling CFM and zero minimum CFM to maintain required space temperature setpoint.

Variable Volume Air Terminal Unit with Reheat Coil:

A space temperature sensor and occupancy sensor shall signal the DDC controller, which shall modulate the air damper between its cooling maximum, low minimum, and heating maximum CFM to maintain the required space temperature setpoint +/- occupied dead band.

When the airflow has reached its scheduled minimum and the space temperature remains below setpoint, the hot water coil valve shall be modulated and the airflow increased to the heating airflow to maintain the required space temperature setpoint +/- occupied dead band.

Carbon dioxide sensors described in the air handling unit sequence above shall signal the DDC controller, which shall reset the minimum CFM setpoint of all terminal units to the high minimum CFM value.  The CFM setpoint shall be reset to the low minimum CFM value when the carbon dioxide level drops below 800 PPM (adjustable).

Terminal units with occupancy sensors shall adjust the temperature setpoint dead band based on occupancy.  When occupied, use the occupied dead band.  When unoccupied, use the unoccupied dead band.  The occupied mode shall have a minimum duration time prior to switching to the unoccupied mode.  There shall be no minimum duration time for the unoccupied mode.

The occupancy sensor shall have an occupancy override button, which shall signal the DDC controller, which shall change the occupancy state to “occupied.”  Pushing the occupancy override button shall not switch the occupancy state to unoccupied.

Space temperature setpoint, occupied dead band, unoccupied dead band, and occupied mode duration time shall be adjustable inputs.

Cabinet Unit Heaters and Unit Heaters:  A unit-mounted line voltage thermostat (furnished with unit) shall open the normally open heating coil valve and cycle the fan to maintain the required setpoint.

Typical of restroom, smoking room, machine room, and similar exhaust fans.

General Area Exhaust Fans:

The exhaust fans shall operate when the air handling units are in the occupied mode.

The exhaust fans shall not operate when air handling units are all in the shutdown mode.

A current transformer located in the fan power circuit shall signal the DDC controller, which shall generate an alarm in the event of fan/control failure.

Sanitation Bay Exhaust Fan:

The exhaust fan shall operate continuously.

A current transformer located in the fan power circuit shall signal the DDC controller, which shall generate an alarm in the event of fan/control failure.

Bag Road Exhaust Fans:

The fan shall be cycled by the DDC controller according to a time clock schedule.

The normally closed damper shall be opened before the fan is started.

A current transformer located in the fan power circuit shall signal the DDC controller, which shall generate an alarm in the event of fan/control failure.

Loss of Power:  The DDC controller shall sequence the restarting of all motors in the event of a loss of power to limit the current draw.

Elevator Shaft Vent:  The elevator hoist way vent shall be manually controlled.

Elevator and Tunnel Sumps:  A float type level switch located in the sump shall signal the DDC controller, which shall generate an alarm in the event of high water level.

Typical of main electrical room.

Constant volume air handling unit with cooling coil and outside and return air dampers for economize control:

Occupied Cycle:

The supply fan shall run continuously.

A space temperature sensor shall signal the DDC controller, which shall modulate the normally open return damper, normally closed outside air damper and normally open chilled water coil valve in sequence to maintain an 85ºF (adjustable) space temperature.  The DDC controller shall generate an alarm if the room temperature deviates from the setpoint by more than 5ºF.

Outside air and return air temperature sensors shall signal the DDC controller.  The outside air and return air dampers shall return to their minimum positions when the outside air temperature exceeds the return air temperature.

Shutdown Mode:  When the air handling unit is not in operation, the following conditions shall exist:

The supply and exhaust fans shall not operate.

All dampers and valves shall be in their normal, de-energized positions.

Alarms/Safeties:

A low limit detection thermostat located on the upstream side of the cooling coil shall signal the DDC controller, which shall initiate the shutdown mode upon sensing a temperature below 40ºF (adjustable).  An alarm shall be generated.

A differential pressure switch located across the filter bank shall signal the DDC controller, which shall generate an alarm when the static pressure drop exceeds 0.5 inches W.G. (adjustable).

A current transformer located across the supply fan power circuit shall signal the DDC controller, which shall generate an alarm in the event of fan/control failure.

A manual reset static pressure switch located in the mixing plenum shall be hard-wired to shut down the supply fan in the event that the static pressure exceeds -2.0 inches W.G. (adjustable).

Finned Tube Radiation:

Low voltage electric thermostat shall cycle the normally open, two-position, two-way control valve to maintain a 70ºF (adjustable) room temperature.

The DDC controller shall open the normally open control valve when the outside air temperature is below 50ºF (adjustable).

Sanitation Bay Slab Heat:

Pump shall be started and stopped by the DDC control system.  The pump shall operate when the outside air temperature is below 40ºF (adjustable).

A current transformer located in the pump power circuit shall signal the DDC control system which shall generate an alarm in the event of pump/control failure.

A temperature sensor located in the slab shall signal the DDC controller, which shall modulate the normally closed two-way heating water control valve to maintain a 40ºF (adjustable) slab temperature.

A temperature sensor located in the HWS piping at the pump discharge shall signal the DDC controller, which shall limit the HWS temperature to 140ºF (adjustable).  An alarm shall be generated if the HWS temperature rises above 145ºF (adjustable).

Typical of concourse walkway rooftop package HVAC unit.

Package rooftop air-conditioning unit with DX cooling coil and hot water heating coil:

Roof-Mounted Package Air-Conditioning Unit:  The RTU shall be controlled by a Metasys-compatible non-programmable thermostat capable of automatically sequencing outside and return air dampers, modulating hot water coil or DX cooling coil control valve to maintain room temperature.  Controls shall be capable of operator programmed night setback, 7-day time clock operation, and morning warm-up cycle.  Controls shall be capable of maintaining space static pressure by operating relief exhaust fan dampers.  Units are designed to be run 24 hours a day.

Economizer:  Wet bulb controlled type.  Outside air and return air dampers modulate to maintain discharge temperature on call for cooling.  Provide automatic adjustable minimum outside air damper position set to maintain a constant air flow over range of unit airflow.

Low-Ambient Compressor Lockout:  Provide compressor lockout stat to prevent compressor operating during economizer mode, and heating.

Smoke Detectors shall prevent fan operation and close return and supply dampers upon detection.  Locate detector in supply air downstream of filters.  The smoke detectors shall also send an alarm to the DDC system.

Typical of EOC/Comm Center backup AHU unit.

Variable speed roof-mounted package air-conditioning unit with hot water coil and DX cooling coil:

Roof-Mounted Package Air-Conditioning Unit:  The RTU shall be controlled by a stand-alone microprocessor-based controller capable of automatically sequencing outside and return air dampers, modulating hot water coil or DX cooling coil control valve to maintain discharge temperature.  Controls shall be capable of operator programmed night setback, 7-day time clock operation, and morning warm-up cycle.  Controls shall be capable of maintaining space static pressure by operating relief exhaust fan VSD.  Units are designed to run 24 hours a day.

Economizer:  Wet bulb controlled type.  Outside air and return air dampers modulate to maintain discharge temperature on call for cooling.  Provide automatic adjustable minimum outside air damper position set to maintain a constant air flow over range of unit airflow.

Duct Static Pressure Control:  A remote duct static pressure sensor shall signal control panel to modulate the supply fan variable speed controller to maintain set static pressure.  Air balancer to determine final set static, initial setting of 0.75 inch W.G. (adjustable).  Shutdown fan on duct static pressures above 2 inch W.G.

Building Static Pressure Control:  Space to outdoor differential static pressure sensor shall signal control panel to modulate the relief exhaust fans variable speed controller to maintain space static pressure relative to outdoors at plus 0.02 inch W.G. differential.

Space Temperature Control:  Refer to terminal unit control sequence.

Low-Ambient Compressor Lockout:  Provide compressor lockout stat to prevent compressor operating during economizer mode, and heating.

Smoke detectors shall prevent fan operation and close return and supply dampers upon detection.  Locate detector in return air.  The smoke detectors shall also send an alarm to the DDC system.

Interface with DDC:  Control panel for each unit shall be capable of interfacing with other local controllers on the DDC system.  Interface shall be capable of communicating the following (variable) analog inputs/outputs and digital I/O.

Analog inputs to unit controller from DDC:

SA cooling setpoint.

SA heating setpoint.

Space static pressure setpoint.

SA static pressure setpoint.

Start/stop.

Digital output from unit controller to DDC:

Dirty filters.

Compressor fault.

Heat fault.

Supply fan fault.

Return/exhaust fan fault.

Run status.

Start/stop.

Steam-to-Hot Water Heat Exchangers:

A hot water supply temperature sensor located in the common supply header shall signal the DDC controller, which shall sequence the two normally closed two-way steam control valves at the lead heat exchanger to maintain a 190ºF (adjustable) hot water supply temperature.

Upon failure of the lead heat exchanger to maintain the hot water supply (HWS) temperature setpoint, the steam control valves on the lag heat exchanger shall be activated as described above.

A hot water supply temperature sensor located in each heat exchanger shall signal the DDC controller.  Upon failure of the lead or lag heat exchanger to maintain its individual HWS temperature setpoint, the steam control valves of that heat exchanger shall be closed and the backup heat exchanger valves shall be activated as described above.

The lead, lag and backup heat exchangers shall be designated and selectable by the operator’s terminal software command.

Variable Speed Duplex Heating Hot Water Pumps:

The lead pump shall run continuously.

A differential pressure switch located across the pumps shall signal the DDC controller when the differential pressure drops below the acceptable limit (adjustable).  An alarm shall be generated.

Differential pressure sensors across the HWS and hot water return (HWR) piping at indicated locations in the piping system shall signal the DDC controller, which shall signal the variable speed controller to adjust the speed of the lead pump to maintain the setpoints at each differential pressure sensor.

A water flow meter shall signal the DDC controller, which shall report the HWS flow instantaneously and over time.

Upon failure of the lead pump, the standby pump shall be started.  Operating time shall be divided between the pumps.

The DDC controller shall interface with variable speed controller to monitor pump rpm and drive failure.

The DDC controller shall monitor rpm and gpm and shall not operate the pump at or beyond its published “end of curve.”

Variable Speed Triplex Hot Water Heating Pumps:

The lead pump shall run continuously.

A differential pressure sensor located across the pumps shall signal the DDC controller when the differential pressure drops below the acceptable limit (adjustable).

Differential pressure sensors across the HWS and HWR piping at indicated locations in the piping system shall signal the DDC controller, which shall signal the variable speed controller to adjust the speed of the pumps to maintain the setpoints at each differential pressure sensor.

Upon failure of the lead pump to maintain the differential pressure setpoints, the lag pump shall be started.

A water flow meter shall signal the DDC controller, which shall report to the HWS flow instantaneously and over time.

Upon determination that the lead pump is capable of satisfying the flow requirements of the system, the DDC controller shall shut down the lag pump.

Upon failure of the lead or lag pump, the standby pump shall be started.  Operating time shall be divided between the pumps.

The DDC controller shall interface with variable speed controller to monitor pump rpm and drive failure.

The DDC controller shall monitor rpm and gpm and shall not operate the pumps at or beyond their published “end of curve.”

The DDC controller shall monitor rpm and gpm and shall stage the pumps to maximize pumping system efficiency and minimize energy consumption at all system operating conditions.

Condensate Return Units:  Factory packaged controls shall cycle the unit pumps as required.

Steam Door Heaters:

The fan shall operate continuously when the outside air temperature is below 40ºF (adjustable).

A temperature sensor located in the air intake to the door heater shall signal the DDC controller, which shall modulate the normally open steam coil valve to maintain a 50ºF (adjustable) air temperature.

A current transformer located in the fan power circuit shall signal the DDC controller, which shall generate an alarm in the event of fan failure.

Typical of Concourse C extension temporary boiler.

Packaged, Gas-Fired Water Tube Boiler:

The boilers shall be started and stopped by the DDC controller.  Under normal operation the lead boiler shall operate continuously.  The lead and lag boilers shall be cycled to divide time evenly between the boilers.

Packaged boiler controls shall control the boiler to maintain the HWS temperature setpoint.

A system HWS temperature sensor shall signal the DDC controller, which shall reset the HWS temperature linearly from 180ºF at 30ºF outside air to 140ºF at 65ºF outside air (adjustable).

The DDC controller shall start the lag boiler when the system HWS temperature setpoint can no longer be met by the lead boiler.  The DDC controller shall shut down the lag boiler when the temperature difference between the system HWS and HWR indicates that the load could be met by one boiler.

The boiler shall signal the DDC controller in the event of failure.  An alarm shall be generated.

An HWS and HWR temperature sensor shall signal the DDC controller.

The boilers shall not operate upon failure of the heating water pumps.

A pushbutton switch located outside the door to the boiler room shall signal the DDC controller which shall shut the boiler down and disconnect all power to the boiler burner controls and generate an alarm.  The switch shall be labeled “Emergency Boiler Shutdown Switch.”

Typical of Concourse C extension temporary heating hot water system.

Stand-alone, constant speed, heating water pump for use with packaged gas-fired water tube boilers:

The DDC controller shall start and stop the pumps.  During normal operation the lead pump shall operate continuously.  The DDC controller shall cycle the lead and lag pumps to divide time evenly between the pumps.

The DDC controller shall start the lag pump when the system HWS temperature can no longer be met by the lead boiler.  The lag pump shall be shut down when the lag boiler is no longer required as described above.

A current transformer located in the pump power circuit shall signal the DDC controller, which shall generate an alarm in the event of pump/control failure.

Typical of Concourse C extension temporary chilled water system.

Packaged Air-Cooled, Water Chiller:

The DDC controller shall start and stop the chillers.  The chillers shall be enabled for operation when the outside air temperature is above 60ºF (adjustable).  The DDC controller shall cycle the lead and lag chillers to divide operating time evenly between the chillers.

An evaporator flow switch shall be hard-wired to prevent the chiller from operating upon loss of flow.

Packaged unit controls shall operate the chiller to maintain the chilled water supply setpoint.  The setpoint shall be adjustable by the DDC controller.

Chilled water temperatures in the system chilled water supply (CHWS) and chilled water return (CHWR) piping shall signal the DDC controller.

The DDC controller shall start the lag chiller when the system CHWS temperature can no longer be met by the lead chiller.  The DDC controller shall shut down the lag chiller when the temperature difference between the system CHWS and CHWR indicates that the load could be met by the lead chiller.

A CHWS temperature sensor at each chiller shall signal the DDC controller.

The chiller shall signal the DDC controller in the event of chiller failure.  An alarm shall be generated.

For use with packaged, air-cooled, water chillers.

Stand-Alone Constant Speed, Chilled Water Pumps:

The DDC controller shall start the lead pump when the outside air temperature is above 60ºF (adjustable).  The DDC controller shall cycle the lead and lag pumps to divide time evenly between the pumps.

The DDC controller shall start the lag pump when the system CHWS temperature can no longer be met by the lead chiller.  The lag pump shall be shut down when the lag chiller is no longer required as described above.

A current transformer located in the pump power circuit shall signal the DDC controller, which shall generate an alarm in the event of pump/control failure.

Typical of Concourse C extension temporary boiler room.

Combustion Air Supply Fan:

The DDC controller shall start and stop the fan.  Under normal operation the fan shall operate continuously.

A current transformer located in the fan power circuit shall signal the DDC controller, which shall generate an alarm in the event of fan/control failure.

Typical of EOC/Comm Center backup hot water boiler.

Packaged Electric Hot Water Boilers:

The boilers shall be controlled by packaged unit controls and boiler management system (BMS) control panel.  Coordinate with boiler manufacturer’s representative to set up required sequences of operation.

The DDC controller shall enable operation of each boiler.  Under normal operation all boilers shall be enabled.

The boilers shall signal the DDC system in the event of failure.  An alarm shall be generated.

An HWS and HWR temperature sensor shall signal the DDC controller.

The boilers shall not operate when both heating water pumps are not operating.

For use with packaged electric hot water boilers.

Stand-Alone, Constant Speed, Heating Water Pumps:

The lead pump shall run continuously.

A current transformer located in the pump power circuit shall signal the DDC controller, which shall generate an alarm in the event of pump/controller failure.

Upon failure of the lead pump, the standby pump shall be started.  Operating time shall be divided between the pumps.

Differential pressure sensors across the HWS and HWR piping at indicated locations in the piping system shall signal the DDC controller, which shall modulate the 2-way control valve located across the bypass to maintain the setpoints at the differential pressure sensor.

Domestic Hot Water Recirculation Pumps:

The DDC controller shall operate pumps during occupied cycles as determined by time of day scheduled and operator input.

The DDC controller shall generate an alarm upon pump failure.

Fire Alarm Shutdown:  A signal from the fire alarm zone shall signal the DDC controller to initiate the shutdown mode of the indicated air handling unit and close all associated combination fire/smoke dampers in the supply and return ductwork.

Packaged Air-Conditioning Units:

A Metasys-compatible non-programmable thermostat shall control the unit to maintain the space temperature setpoint.

Steam PRV Control:  The steam pressure regulating controls shall maintain the pressure of the low pressure steam header at a setpoint of 15 psig.  This shall be accomplished by modulating two control valves using two single-loop PID controllers.

Typical of MAU for ventilation ARFF vehicle apparatus bay.

Gas-Fired Makeup Air Unit:

General:  Interface with unit factory controls.  Field modify as required.  Provide outside air damper operator.

Occupied Cycle:

The DDC controller shall cycle the unit on a time-based schedule (adjustable).  Carbon monoxide sensors located in the area(s) serviced by the MAU shall override the time-based schedule and the unit shall operate when the carbon monoxide level exceeds 50 PPM (adjustable).

The normally closed outside air damper shall be open.

A discharge air temperature sensor shall signal the DDC controller, which shall control the gas modulator/regulator valve (integral to unit) to maintain the required discharge air temperature (60ºF, adjustable).  The discharge temperature control shall be overridden and reset upward when space temperature sensors remain below setpoint for duration of time (adjustable).

Shutdown Mode:  When the unit is not in operation, the following conditions shall exist:

The supply fan shall not operate.

All dampers and valves shall be in their normal de-energized positions.

Alarms/Safeties:

A smoke detector located in the supply air duct shall signal the DDC controller, which shall initiate the shutdown mode upon detection of smoke in the airstream.  An alarm shall be generated.

The discharge air temperature sensor shall signal the DDC controller, which shall initiate the shutdown mode upon sensing a temperature below 40ºF (adjustable).  An alarm shall be generated.

A differential pressure switch located across the filter bank shall signal the DDC controller, which shall generate an alarm when the static pressure drop exceeds 0.75 inches W.G. (adjustable).

Current transformers located in the fan power circuit shall signal the DDC controller, which shall generate an alarm in the event of fan/control failure.

Verify section number below is used in the project.

Gas-Fired Unit Heater:  Refer to Section 235523, Gas-Fired Radiant Heater.  Provide wiring as required.

Verify section number below is used in the project.

Gas-Fired Duct Furnace:  Refer to Section 235500, Fuel-Fired Heaters.  Provide wiring as required.

Radiant Heaters RH-1:  Space temperature sensors shall signal the DDC controller, which shall cycle the heaters to maintain the average required space temperature setpoint.  Interface with unit factory controls.  Field modify as required.

SYSTEM BALANCE, CONTROL VALVE, AND TEMPERATURE SCHEDULES

The System Balance and Control Valve Schedule and Temperature Schedule are included at the end of this section.

| SYSTEM BALANCE AND CONTROL VALVE SCHEDULE |
| --- |
| System Components | System Design Parameters | Pump Balancing Parameters | Control Valve Parameters |
|  | Current Max Flow (GPM) | Future Max Flow (GPM) | Scheduled Pump Flow (GPM) | Min Flow (GPM) | Min Flow Provided By | Balance Pump (GPM) | Notes | Valve Name | Valve Type | Valve Qty | Max Total (GPM) | Min Total (GPM) |
| Chiller Primary Loop Components | Chiller Condenser/ HW Primary | 680 | 760 | 765 | 85 | 1 chiller module, both heat exchangers | 680 | Chiller max flow | Primary HW Bypass Valve | 3-way | 2 | 760 | 85 |
|  | Chiller Evaporator/ CHW Primary | 1014 | 1140 | 1140 | 127 | 1 chiller module, both heat exchangers | 1014 | Chiller max flow | Primary CHW Bypass Valve | 3-way | 2 | 1140 | 127 |
| Heat Rejection Secondary Components | Ground Well/ WW Secondary | 960 | 960 | 960 | 80 | 1 zone open or end of line bypass | 960 | N/A | Cooling Tower Zone Valve | 2-way, 2-position | 1 | 115 | 115 |
|  |  |  |  |  |  |  |  |  | Well Zone Valve | 2-way | 1 per zone, 13 zones | Dependent on well zone as-built, 4.75 GPM per well | 80% max to prevent laminar flow |
| Secondary Components | Heating Water Loop/ HW Secondary | 700 | 700 | 700 | 90 | Sum at end of line bypass | 700 | Balance for all valves open may not be exact | TU, CUH, AHU, FCU | 2-way | 1 per component | Flow shown for component | 10% scheduled |
|  |  |  |  |  |  |  |  |  | Secondary HW Bypass Valve | 2-way | 1 | 250 | 90 |
|  |  |  |  |  |  |  |  |  | Radiant HW Valve | 2-way | 1 | 233 | 30 |
|  | Chilled Water Loop/ CHW Secondary | 1000 | 1000 | 1000 | 125 | Base cooling load and/or sum of end of line bypass | 1000 | Balance for all valves open may not be exact | AHU, FCU | 2-way | 1 per component | Flow shown for component | 10% scheduled |
|  |  |  |  |  |  |  |  |  | Secondary HW Bypass Valve | 2-way | 1 | 350 | 125 |
|  |  |  |  |  |  |  |  |  | Radiant CHW Valve | 2-way | 1 | 300 | 40 |
| Tertiary Components | Radiant Water Loop/ HW Secondary | 605 | 650 | 600 | 75 | Sum of end of line bypass | 600 | 10% diversity in system | VCU/FCU Heating Coil Valve | 2-way | 1 per component | Flow shown for component | 10% scheduled |
|  | Radiant Water Loop/ CHW Secondary | 830 | 780 | 700 | 90 | Sum of end of line bypass | 700 | 10% diversity in system | Radiant Zone Valve | 2-way | 1 per component | Flow shown for component | 50% scheduled to prevent laminar flow |
|  | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | Radiant Diverting Valve | 3-way, 2-position | 2 per component (1 supply, 1 return) | Flow shown for component | Same as max |
| Notes: 1. See drawings for valve callouts using the same name indicated on this schedule. 2. End of line bypass valves size shall be as shown on the drawings. 3. Pumps to be balanced for future flow shall operate at reduced speed to match current flow at the end of this project. 4. There is diversity in the heating and chilled water secondary and tertiary loops. The sum of the component flows does not exactly match the pump flows. 5. All 2-way modulating valves shall be delta-P valves. 6. All 2-position valves shall be line size, full open. |

| SYSTEM TEMPERATURE RANGE AND SETPOINT SCHEDULE |
| --- |
| System Components | Design Temperatures | Setpoint Reset and Control |
|  |  | EWT (°F) | LWT (°F) | Min Setpoint (°F) | OSA Lockout (°F) | Max Setpoint (°F) | Normal Operations | Override Control |
| Chiller Primary Loop Components | Chiller Condenser/ HW Primary | 105 | 125 | 7 | N/A | 125 | Based on secondary setpoint control | N/A |
|  | Chiller Evaporator/ CHW Primary | 48 | 38 | 38 | N/A | 53 | Based on secondary setpoint control | N/A |
| Heat Rejection/ Collection Secondary Components | Ground Well/ Secondary Heat Collection | 38 | 48 | 45 | N/A | N/A | Primary CHW bypass valves 90% open | N/A |
|  | Ground Well/ WW Secondary | 125 | 105 | 70 | N/A | 105 | Primary HW bypass valves 90% open | N/A |
|  | Heat Rejection/ Cooling Tower CD | 125 | 105 | 60 | 40 | 105 | WWS temp -10°F | Lockout if not < 5°F from WWS |
| Secondary Components | Heating Water Loop/ HW Secondary | 103 | 123 | 85 | 65 | 123 | Most open zone valve, 90% open, one valve | N/A |
|  | Chilled Water Loop/ CHW Secondary | 55 | 40 | 40 | N/A | 55 | Most open zone valve, 90% open, one valve | Based on space %RH and temp sensor calc, reset to min setpoint |
| Tertiary Components | Radiant Water Loop/ HW Secondary | 110 | 100 | 85 | 65 | 110 | Most open zone valve, 90% open, one valve | N/A |
|  | Radiant Water Loop/CHW Secondary | 55 | 60 | 55 | 60 | 70 | Most open zone valve, 90% open, one valve | Space temp/ %RH sensor calc, 1°F above calc |

END OF SECTION 230900