## SCHEDULE
Directions:
1. The kitchen equipment descriptions and electrical characteristics will be provided by the project kitchen consultant
2. The electrical designer will copy only the kitchen equipment items with electrical requirements into the schedule.
3. The kitchen equipment tags will match the tags provided on the kitchen consultants documents.
4. Provide a corresponding equipment tag on the kitchen plans, using a oval symbol.
5. Provide the standard hood fire suppression monitoring and shutdown detail on the drawings
6. Fill out the blue portion below and insert into the design drawing package.
Project: | XYZ | [6 empty] | Orig. Date: | 1/1/1111
[8 empty] | Revised: | 1/1/1111
Architect: | XYZ | [6 empty] | By: | XYZ
Kitchen Consultant: |  | XYZ | [5 empty] | Chk By: | XYZ
KITCHEN EQUIPMENT CONNECTION SCHEDULE
EQUIPMENT DESCRIPTIONS |  |  | ELECTRICAL CHARACTERISTICS |  |  |  | FEEDER CHARACTERISTICS |  |  |  |  | PANEL INFORMATION |  | EQUIPMENT CONNECTION |  | NOTES
EQUIPMENT ID TAG | DESCRIPTION | LOCATION | LOAD (KW) | LOAD (AMPS) | VOLTS | PHASE | CONDUIT | PHASE CONDUCTORS | GROUND CONDUCTORS | OCP | DISCONNECT | PANEL | CIRCUIT | TYPE | LOCATION
1 | REMOTE REFRIGERATION SYSTEM |  |  | 150 | 208 | 3 | 2" | 3#3/0 | 1#6 | 200/3 |  |  |  | HARDWIRE
3 | SODA RACK |  |  | 10 | 120 | 1 | 3/4" | 2#12 | 1#12 | 20/1 |  |  |  | NEMA 5-20R
14 | FOOD WASTE COLLECTOR |  |  | 3.2 | 208 | 3 | 3/4" | 3#12 | 1#12 | 20/3 |  |  |  | HARDWIRE
18 | DISHWASHER |  |  | 55 | 208 | 3 | 1-1/4" | 3#1 | 1#6 | 125/3 |  |  |  | HARDWIRE
29 | MOBILE HEATED CABINET |  |  | 16 | 120 | 1 | 3/4" | 2#12 | 1#12 | 20/1 |  |  |  | NEMA 5-20R
34 | WALK-IN FREEZER |  |  | 10 | 120 | 1 | 3/4" | 2#12 | 1#12 | 20/1 |  |  |  | HARDWIRE
35 | EVAPORATOR COIL |  |  | 1.8 | 208 | 1 | 3/4" | 3#12 | 1#12 | 20/2 |  |  |  | HARDWIRE
36 | WALK IN FREEZER |  |  | 10 | 120 | 1 | 3/4" | 2#12 | 1#12 | 20/1 |  |  |  | HARDWIRE
37 | EVAPORATOR COIL |  |  | 1.8 | 208 | 1 | 3/4" | 3#12 | 1#12 | 20/2 |  |  |  | HARDWIRE
41 | WALK-IN COOLER |  |  | 10 | 120 | 1 | 3/4" | 2#12 | 1#12 | 20/1 |  |  |  | HARDWIRE
43 | EVAPORATIVE COIL |  |  | 2 | 120 | 1 | 3/4" | 2#12 | 1#12 | 20/1 |  |  |  | HARDWIRE
45 | WORK TABLE |  |  | 15 | 120 | 1 | 3/4" | 2#12 | 1#12 | 20/1 |  |  |  | NEMA 5-20R
47 | WORK TABLE |  |  | 15 | 120 | 1 | 3/4" | 2#12 | 1#12 | 20/1 |  |  |  | NEMA 5-20R
48 | MEAT SLICER |  |  | 5.6 | 120 | 1 | 3/4" | 2#12 | 1#12 | 20/1 |  |  |  | NEMA 5-20R
51 | WORK TABLE |  |  | 15 | 120 | 1 | 3/4" | 2#12 | 1#12 | 20/1 |  |  |  | NEMA 5-20R
52 | WORK TABLE |  |  | 15 | 120 | 1 | 3/4" | 2#12 | 1#12 | 20/1 |  |  |  | NEMA 5-20R
GENERAL NOTES: (SOME MAY NOT BE USED ON THIS SHEET)
A. REFER TO THE KITCHEN CONSULTANT DOCUMENTS FOR FURTHER DETAILS, NOTES AND ELECTRICAL INSTALLATION INSTRUCTIONS.
B. ALL RECEPTACLES WITHIN THE KITCHEN AREA SHALL BE GFCI TYPE PER NEC.
NOTES: (SOME MAY NOT BE USED ON THIS SHEET)
1. PROVIDE CONTROLS INTERLOCK CONNECTION BETWEEN THE HOOD CONTROL PANEL AND THE HOOD EXHAUST FAN STARTER AS RECOMMENDED BY THE HOOD MANUFACTURER
2. PROVIDE CONTROLS INTERLOCK CONNECTION BETWEEN THE DISHWASHER CONTROL PANEL AND THE HOOD EXHAUST FAN STARTER AS RECOMMENDED BY THE DISHWASHER MANUFACTURER
3. PROVIDE POWER AND GAS SHUTOFF FOR EQUIPMENT LOCATED UNDER THE HOOD, REFER TO DETAIL ______________
4. PROVIDE FIRE ALARM SYSTEM MONITORING OF THE HOOD FIRE SUPRESSION PANEL, REFER TO DETAIL _____________
5. FOR EACH PIECE OF HARDWIRED EQUIPMENT, PROVIDE SUITABLE DISCONNECTING MEANS IN ACCESSIBLE, CONCEALED SEPARATE LOCATION
WITHIN LINE OF SIGHT OF EQUIPMENT. DISCONNECT MAY BE OMITTED IF EQUIPMENT HAS SUITABLE INTEGRAL DISCONNECTING MEANS.

## Sheet1
TAG | ITEM NO | QTY | EQUIPMENT CATEGORY | LOCATION | MANUFACTURER | MODEL NUMBER | EQUIPMENT REMARKS | VOLTS | PHASE | AMPS | KW | HP | NEMA | ELECTRICAL AFF (IN)
| 1 | 1 | WALK-IN FREEZER/COOLER |  | CUSTOM | CUSTOM |  | 120 | 1 | 15 |  |  |  | 108
| 2 | 1 | FREEZER COMPRESSOR |  | HEATCRAFT | M0H025L63S |  | 208 | 3 | 21 |  | 2.5
| 3 | 1 | FREEZER EVAPORATOR |  | HEATCRAFT | LSF090SB-EC |  | 208 | 1 | 7.8 |  |  |  | 84
| 5 | 1 | COOLER COMPRESSOR |  | HEATCRAFT | M0H01X63S |  | 208 | 3 | 15 |  | 1
| 6 | 1 | COOLER EVAPORTAR |  | HEATCRAFT | LSC090SA-EC |  | 115 | 1 | 1.8 |  |  |  | 84
| 12 | 1 | ICE MAKER W/ BIN |  | MANITOWOC ICE | SY-0855W /B-570 |  | 208 | 1 | 10.3 |  | 1.5 |  | 73
| 15 | 1 | VEGETABLE CUTTER |  | ROBOT COUPE | R2C | OFCI | 120 | 1 | 7 |  | 0.5 | 5-15P
| 18 | 1 | REACH-IN FREEZER |  | TRAULSEN | ALT126WUT-FHS |  | 115 | 1 | 11.5 |  | 0.5 | 5-15P | 77.5
| 20 | 1 | REACH-IN REFRIGERATOR |  | TRAULSEN | ALT226WUT-FHS |  | 115 | 1 | 8.5 |  | 0.33333 | 5-15P | 77.5
| 21 | 1 | BLAST CHILLER |  | RANDELL | BC-5E |  | 120 | 1 | 16 |  | 0.5 | 5-20P | 6
| - | - | - |  | - | - |  | 208 | 3 | 30 | 10.8
| 26 | 1 | TILT SKILLET |  | CLEVELAND RANGE | SEL40T1 |  | 208 | 3 | 50 | 18 |  |  | 22.5
| 28 | 1 | ELECTRIC HEAVY DUTY RANGE |  | LANG MANUFACTURING | R36B-ATD |  | 208 | 3 | 66.7 | 21 |  |  | 8
| 29 | 1 | INDUCTION COOKER |  | COOKTEK | MC3502F |  | 208 | 1 | 30 | 7 |  | 6-50P
| 29 | 1 | INDUCTION COOKER |  | COOKTEK | MC3502F |  | 208 | 1 | 30 | 7 |  | 6-50P
| 33 | 1 | ELECTRIC CONVECTION OVEN |  | LANG MANUFACTURING | 2ECC0-SII |  | 208 | 3 | 74.2 | 23.3
| 33 | 1 | ELECTRIC CONVECTION OVEN |  | LANG MANUFACTURING | 2ECC0-SII |  | 208 | 3 | 74.2 | 23.3
| 37 | 1 | DRAWER WARMER |  | HATCO | HDW-2B |  | 120 | 1 | 7.5 | 0.9
| 54 | 1 | CONVEYER WAREWASHER |  | AMERICAN DISH SERVICES | ADC-44 |  | 208 | 3 | 60 | 14.3 | 3.6667 |  | 63.5
| 66 | 1 | MOBILE WARMING & HOLDING CABINET |  | CRES COR | H-137-WSUA-12C |  | 120 | 1 | 16 | 2 |  | 5-20P | 70.9
| 101 | 1 | AUTOMATIC COFFEE MAKER |  | FETCO | CBS-51H | OFCI | 120 | 1 | 15.5 | 1.9 |  | 5-20P
| 102 | 1 | COFFEE GRINDER |  | FETCO | - | OFCI | 120 | 1 | 5.2 | 0.5 | 0.67

## Sheet3
KITCHEN AND LAUNDRY EQUIPMENT CONNECTION SCHEDULE
TAG | DESCRIPTION | LOCATION | LOAD | VOLTS | PHASE | CONDUIT | CONDUCTOR | PANEL-CIRCUIT | OCP | STARTER | DISCONNECT | EQUIPMENT CONNECTION
[12 empty] | TYPE | LOCATION | HEIGHT | NOTES
K1A | (2) WALK-IN LIGHTS | COOLER 119 | 160W | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-19 | 30AS/2AF | - | FUSED | J-BOX | CEILING |  | NOTE 3
K1B | (2) WALK-IN LIGHTS | COOLER 118 | 160W | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-19 | 30AS/2AF | - | FUSED | J-BOX | CEILING |  | NOTE 3
K2 | (4) WALK-IN LIGHTS | FREEZER 117 | 320W | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-19 | 30AS/3AF | - | FUSED | J-BOX | CEILING |  | NOTE 3
K3 | WALK-IN DRAIN LINE HEATER | FREEZER 117 | 500W | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-21 | 30AS/5AF | - | FUSED | J-BOX | CEILING |  | NOTE 3
K4 | WALK-IN DOOR HEATER | FREEZER 117 | 500W | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-21 | 30AS/5AF | - | FUSED | J-BOX | CEILING |  | NOTE 3
K5 | WALK-IN COOLER EVAPORATOR | COOLER 119 | 360W | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-1 | 30AS/3AF | - | FUSED | J-BOX | CEILING |  | NOTE 3
K6 | WALK-IN COOLER EVAPORATOR | COOLER 118 | 360W | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-1 | 30AS/3AF | - | FUSED | J-BOX | CEILING |  | NOTE 3
K7 | WALK-IN FREEZER EVAPORATOR | FREEZER 117 | -- | -- | -- | 1/2" | 2#12,1#12G | -- | -- | - | NON-FUSED | J-BOX | CEILING |  | NOTE 1
K8 | WALK-IN COOLER CONDENSING UNIT | ROOF | 12FLA | 208 | 3 | 3/4" | 3#8, 1#10G | LSK-2/4/6 | 30AS/15P | - | FUSED | J-BOX | ROOF |  | NOTE 3
K9 | WALK-IN COOLER CONDENSING UNIT | ROOF | 12FLA | 208 | 3 | 3/4" | 3#8, 1#10G | LSK-2/4/6 | 30AS/15P | - | FUSED | J-BOX | ROOF |  | NOTE 3
K10 | WALK-IN FREEZER CONDENSING UNIT | ROOF | 49FLA | 208 | 3 | 3/4" | 3#8, 1#10G | LSK-18/20/22 | 70A/3P | - | NON-FUSED | J-BOX | ROOF
K11 | CUBE ICE MACHINE | FOOD SERVICE 115 | 1700W | 208 | 3 | 1/2" | 3#12, 1#12G | LNK-2/4/6 | 20A/3P | - | NON-FUSED | J-BOX | WALL | 76" | NOTE 4
K12 | DISPOSER | FOOD SERVICE 115 | 2HP | 480 | 3 | 1/2" | 3#12, 1#12G | HNK-1/3/5 | 15A/3P | - | NON-FUSED | J-BOX | WALL | 24"
K13 | 40 - QUART MIXER | FOOD SERVICE 115 | 1.5HP | 208 | 3 | 1/2" | 3#12, 1#12G | LNK-8/10/12 | 20A/3P | - | NON-FUSED | J-BOX | WALL | 40"
K14 | 20 - QUART MIXER | FOOD SERVICE 115 | 1/2HP | 120 | 1 | 1/2" | 2#12, 1#12G | LNK-17 | 20A/1P | - | - | GFCI, NEMA 5-20R | WALL | 45"
K15 | SLICER | FOOD SERVICE 115 | 1/2HP | 120 | 1 | 1/2" | 2#12, 1#12G | LNK-19 | 20A/1P | - | - | GFCI, NEMA 5-20R | WALL | 45" | NOTE 4
K16 | MICROWAVE OVEN | FOOD SERVICE 115 | 1440W | 120 | 1 | 1/2" | 2#12, 1#12G | LNK-21 | 20A/1P | - | - | GFCI, NEMA 5-20R | WALL | 45" | NOTE 4
K17 | BUFFALO CHOPPER | FOOD SERVICE 115 | 5HP | 208 | 1 | 3/4" | 2#8, 1#10G | LNK-5/7 | 60A/2P | - | NON-FUSED | J-BOX | WALL | 18" | NOTE 4
K18 | FOOD PROCESSOR | FOOD SERVICE 115 | 820W | 120 | 1 | 1/2" | 2#12, 1#12G | LNK-23 | 20A/1P | - | - | GFCI, NEMA 5-20R | WALL | 45" | NOTE 4
K19 | (4) CANOPY HOOD LIGHTS | FOOD SERVICE 115 | 320W | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-23 | 20A/1P | - | NON-FUSED | J-BOX | CEILING |  | NOTES 2,3
K20 | STEAMER | FOOD SERVICE 115 | 720W | 120 | 1 | 1/2" | 2#12, 1#12G | LNK-24 | 20A/1P | - | NON-FUSED | J-BOX | WALL | 16" | NOTE 2
K21 | 40 - GALLON TILTING KETTLE | FOOD SERVICE 115 | 24KW | 480 | 3 | 3/4" | 3#8, 1#10G | HNK-2/4/6 | 40A/3P | - | NON-FUSED | J-BOX | WALL | 16" | NOTE 2
K22 | 40 - GALLON TILTING KETTLE | FOOD SERVICE 115 | 35W | 120 | 1 | 1/2" | 2#12, 1#12G | LNK-29 | 20A/1P | - | NON-FUSED | J-BOX | WALL | 16" | NOTE 2
K23 | TWIN 6 & 10 - GALLON TILTING KETTLES | FOOD SERVICE 115 | 240W | 120 | 1 | 1/2" | 2#12, 1#12G | LNK-28 | 20A/1P | - | NON-FUSED | J-BOX | WALL | 16" | NOTE 2
K24A | DOUBLE STACK CONVECTION OVENS | FOOD SERVICE 115 | 720W | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-8 | 20A/1P | - | - | GFCI, NEMA 5-20R | WALL | 30" | NOTE 2
K24B | DOUBLE STACK CONVECTION OVENS | FOOD SERVICE 115 | 720W | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-12 | 20A/1P | - | - | GFCI, NEMA 5-20R | WALL | 62" | NOTE 2
K25 | MOBILE PROOFING CABINET | FOOD SERVICE 115 | 1900W | 120 | 1 | 1/2" | 2#12, 1#12G | LNK-33 | 20A/1P | - | - | GFCI, NEMA 5-20R | WALL | 45" | NOTE 4
K26 | REACH-IN REFRIGERATOR | FOOD SERVICE 115 | 1308W | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-13 | 20A/1P | - | - | GFCI, NEMA 5-20R | WALL | 86" | NOTE 4
K27 | (4) CANOPY HOOD LIGHTS | FOOD SERVICE 115 | 160W | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-23 | 20A/1P | - | NON-FUSED | J-BOX | CEILING |  | NOTES 2,3
K28 | CANOPY HOOD FIRE PROT. SYSTEM | FOOD SERVICE 115 | 1000W | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-15 | 20A/1P | - | NON-FUSED | J-BOX | WALL | 102"
K29 | FRYERS WITH FILTRATION SYSTEM | FOOD SERVICE 115 | 1000W | 120 | 1 | 1/2" | 2#12, 1#12G | LNK-44 | 20A/1P | - | - | GFCI, NEMA 5-20R | WALL | 14"
K30A | MOBILE REFRIGERATORS | FOOD SERVICE 115 | 1/3HP | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-27 | 20A/1P | - | - | GFCI, NEMA 5-20R | WALL | 18"
K30B | MOBILE REFRIGERATORS | FOOD SERVICE 115 | 1/3HP | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-27 | 20A/1P | - | - | GFCI, NEMA 5-20R | WALL | 18"
K31A | COLD FOOD DISPLAY COUNTER | FOOD SERVICE 115 | 1020W | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-9 | 20A/1P | - | - | GFCI, NEMA 5-20R | FLOOR
K31B | COLD FOOD DISPLAY COUNTER | FOOD SERVICE 115 | 1020W | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-24 | 20A/1P | - | - | GFCI, NEMA 5-20R | FLOOR
K32A | HOT ENTREE COUNTER | FOOD SERVICE 115 | 2500W | 208 | 1 | 1/2" | 2#12, 1#12G | LSK-5/7 | 20A/2P | - | - | NEMA 6-15R | FLOOR
K32B | HOT ENTREE COUNTER | FOOD SERVICE 115 | 2500W | 208 | 1 | 1/2" | 2#12, 1#12G | LSK-26/28 | 20A/2P | - | - | NEMA 6-15R | FLOOR
K33A | POINT OF SALE SYSTEM | FOOD SERVICE 115 | 500W | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-3 | 20A/1P | - | - | GFCI, NEMA 5-20R | FLOOR
K33B | POINT OF SALE SYSTEM | FOOD SERVICE 115 | 500W | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-3 | 20A/1P | - | - | GFCI, NEMA 5-20R | FLOOR
K34 | MOBILE MILK COOLER | FOOD SERVICE 115 | 756W | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-11 | 20A/1P | - | - | GFCI, NEMA 5-20R | FLOOR |  | NOTE 4
K35 | DISPOSER | WAREWASH 116 | 2HP | 480 | 3 | 1/2" | 3#12, 1#12G | HNK-7/9/11 | 15A/3P | - | NON-FUSED | J-BOX | WALL | 24"
K36 | WAREWASHER BOOSTER HEATER | WAREWASH 116 | 30KW | 480 | 3 | 3/4" | 3#8, 1#10G | HSK-2/4/6 | 50A/3P | - | NON-FUSED | J-BOX | WALL | 64"
K37 | WAREWASHER (TANK HEAT/MOTORS) | WAREWASH 116 | 23.5KW | 480 | 3 | 3/4" | 3#8, 1#10G | HSK-8/10/12 | 40A/3P | - | NON-FUSED | J-BOX | WALL | 64"
K38 | COFFEE BREWERS | FOOD SERVICE 115 | 5050W | 208 | 1 | 3/4" | 2#8, 1#10G | LNK-9/11 | 30A/2P | - | NON-FUSED | SINGLE OUTLET | WALL | 45"
-
C1 | COFFEE BREWERS | CATERING 104 | 5050W | 208 | 1 | 3/4" | 2#8, 1#10G | LNK-13/15 | 30A/2P | - | NON-FUSED | SINGLE OUTLET | WALL | 45"
C2 | REACH-IN REFRIGERATOR | CATERING 104 | 1020W | 120 | 1 | 1/2" | 2#12, 1#12G | LSK-29 | 20A/1P | - | - | GFCI, NEMA 5-20R | WALL | 18"
C3 | MICROWAVE OVEN | CATERING 104 | 1600W | 120 | 1 | 1/2" | 2#12, 1#12G | LNK-20 | 20A/1P | - | - | GFCI, NEMA 5-20R | WALL | 45"
L1 | 50 LB WASHER/EXTRACTOR (FUTURE) | LAUNDRY 130 | 20FLA | 208 | 3 | 3/4" | 3#10, 1#10G | LN1D-32/34/36 | 30A/3P | - | NON-FUSED |  | WALL | 60" | NOTE 5
L2A | 50 LB WASHER/EXTRACTOR | LAUNDRY 130 | 20FLA | 208 | 3 | 3/4" | 3#10, 1#10G | LN1D-20/22/24 | 30A/3P | - | NON-FUSED | J-BOX | WALL | 60"
L2B | 50 LB WASHER/EXTRACTOR | LAUNDRY 130 | 20FLA | 208 | 3 | 3/4" | 3#10, 1#10G | LN1D-26/28/30 | 30A/3P | - | NON-FUSED | J-BOX | WALL | 60"
L3A | 75LB DRYER | LAUNDRY 130 | 4.3FLA | 208 | 3 | 1/2" | 3#12, 1#12G | LN1D-8/10/12 | 15A/3P | - | NON-FUSED | J-BOX | WALL | 66"
L3B | 75LB DRYER | LAUNDRY 130 | 4.3FLA | 208 | 3 | 1/2" | 3#12, 1#12G | LN1D-14/16/18 | 15A/3P | - | NON-FUSED | J-BOX | WALL | 66"
L4 | RESIDENTIAL DRYER | LAUNDRY 130 | 24FLA | 208 | 1 | 1/2" | 2#10, 1#10G | LN1D-4/6 | 30A/2P | - | - | NEMA 10-30R | WALL | 48" | NOTE 4
L5 | RESIDENTIAL WASHER | LAUNDRY 130 | 12FLA | 120 | 1 | 1/2" | 2#12, 1#12G | LN1D-31 | 20A/1P | - | - | GFCI, NEMA 5-20R | WALL | 48"
1.) SUPPLY FROM K10. PROVIDE BRANCH CIRCUIT PER MANUFACTURER'S REQUIREMENTS.
2.) PROVIDE SHUNT TRIP CIRCUIT BREAKERS FOR THESE PIECES OF EQUIPMENT. SHUNT TRIP SHALL ACTIVATE UPON INITIATION OF HOOD SUPPRESSION SYSTEM.
3.) EQUIPMENT SHARE THE SAME CIRCUIT. PROVIDE LOCAL FUSE COUPLINGS FOR LIGHTS AND FUSED DISCONNECT SWITCHES FOR EQUIPMENT CONNECTIONS.
4.) OWNER FURNISHED EQUIPMENT. CONFIRM BRANCH CIRCUIT RATING AND RECEPTACLE CONFIGURATION PRIOR TO INSTALLATION.
5.) PROVIDE BRANCH CIRCUIT WIRED TO DISCONNECT SWITCH AS SPECIFIED. NO CONNECTION TO EQUIPMENT REQUIRED. FUTURE CONNECTION.