This master should be used by designers working on Port of Portland construction projects and by designers working for PDX tenants (“Tenants”).  Usage notes highlight a few specific editing choices, however the entire section should be evaluated and edited to fit specific project needs.

# SECTION 333100 - SANITARY UTILITY SEWERAGE PIPING

## GENERAL

DESCRIPTION

This section describes the installation of sanitary sewer piping and related structures.

RELATED WORK SPECIFIED ELSEWHERE

Section 031100, Concrete Formwork

Section 032000, Concrete Reinforcing

Section 033000, Cast-In-Place Concrete

Section  312300, Trenching, Backfilling, and Compacting

REFERENCES

AASHTO:  American Association of State Highway and Transportation Officials

AASHTO M252: Standard Specification for Corrugated Polyethylene Drainage Pipe

AASHTO M278: Standard Specification for Class PS46 Poly(Vinyl Chloride) (PVC) Pipe

AASHTO M294: Standard Specification for Corrugated Polyethylene Pipe, 300- to 1500-mm (12- to 60-in.) Diameter

AASHTO MP7: Standard Specification for Corrugated Polyethylene Pipe, 1350 and 1500 mm Diameter

ASTM:  American Society for Testing and Materials

ASTM A74: Standard Specification for Cast Iron Soil Pipe and Fittings

ASTM A746: Standard Specification for Ductile Iron Gravity Sewer Pipe

ASTM C33: Standard Specification for Concrete Aggregates

ASTM C136: Standard Test Method for Sieve Analysis of Fine and Coarse Aggregates

ASTM C150: Standard Specification for Portland Cement

ASTM C595: Standard Specification for Blended Hydraulic Cements

ASTM C618: Standard Specification for Coal Fly Ash and Raw or Calcined Natural Pozzolan for Use in Concrete

ASTM D2321: Standard Practice for Underground Installation of Thermoplastic Pipe for Sewers and Other Gravity-Flow Applications

ASTM D3034: Standard Specification for Type PSM Poly(Vinyl Chloride) (PVC) Sewer Pipe and Fittings

ASTM D3212: Standard Specification for Joints for Drain and Sewer Plastic Pipes Using Flexible Elastomeric Seals

ASTM D3786: Standard Test Method for Bursting Strength of Textile Fabrics—Diaphragm Bursting Strength Tester Method

ASTM D4491: Standard Test Methods for Water Permeability of Geotextiles by Permittivity

ASTM D4632: Standard Test Method for Grab Breaking Load and Elongation of Geotextiles

ASTM D4751: Standard Test Method for Determining Apparent Opening Size of a Geotextile

ASTM F477: Standard Specification for Elastomeric Seals (Gaskets) for Joining Plastic Pipe

ASTM F758: Standard Specification for Smooth-Wall Poly(Vinyl Chloride) (PVC) Plastic Underdrain Systems for Highway, Airport, and Similar Drainage

AWWA:  American Water Works Association

AWWA C600: Installation of Ductile Iron Water Mains and Their Appurtenances

CISPI:  Cast Iron Soil Pipe Institute

COP:  City of Portland

SUBMITTALS/CERTIFICATIONS

Submit certifications showing that materials meet the requirements shown on the drawings and as specified below.

## PRODUCTS

GROUT

Shall be non-shrink, non-ferrous, non-epoxy with a minimum design strength of 5,000 psi in 28 calendar days.

Use according to manufacturer’s recommendations.

ANTI-SEIZE LUBRICANT

Bolts associated with sanitary utility sewer installation shall be applied with anti-seize lubricant such as Never-Seez, or equal, prior to installation.

CONCRETE STRUCTURES

Construct manholes, catchbasins, and cleanouts as shown on the drawings.

Only use Iron Pipe article if conditions warrant.

IRON PIPE

Note:  Sizes from 2 inches to 15 inches.

Cast Iron Pipe

Pipe and fittings:  Conform to ASTM A74.

Joints shall be push-on or mechanical.

Note:  Sizes from 4 inches to 54 inches.

Ductile Iron Pipe

Pipe and fittings:  Conform to ASTM A746.

Joints shall be push-on or mechanical.

PLASTIC PIPE

Polyvinylchloride (PVC) Pipe

Non-Perforated:  Conform to ASTM D3034.

Perforated:  Conform to ASTM F758, AASHTO M278, or ASTM D3034.  If ASTM D3034 pipe is used, perforate pipe with two rows of 3/8 inch holes located approximately 60 degrees off the bottom on each side, spaced 3 inches on center.

Verify acceptability with jurisdiction involved.

Sanitary Sewer Couplings

Couplings shall meet AASHTO M252, AASHTO M294, and AASHTO MP7; gaskets shall meet ASTM F477.

4- to 48-inch couplings shall be watertight and capable of passing full 10.8 psi ASTM D3212 lab testing.  Joints shall remain watertight when subjected to a 1.5 degree axial misalignment.

BEDDING MATERIAL

Bedding shall be as specified in Section 312300, Trenching, Backfilling, and Compacting.

DRAINAGE GEOTEXTILE

May be monofilament-woven or non-woven.

Split film or slit tape fabrics will not be permitted.

Geotextile shall comply with the following requirements:

| Geotextile Property | Test Method | Minimum Value |
| --- | --- | --- |
| Grab tensile strength, minimum in each principal direction | ASTM D4632 | 80 lbs. |
| Grab elongation | ASTM D4632 | 15 percent |
| Burst strength, diaphragm method | ASTM D3786 | 130 psi |
| Puncture strength | ASTM D3786 modified | 35 lbs. |
| Apparent opening size (AOS) vs. std. sieve | ASTM D4751 | No. 70 sieve or smaller opening |
| Water permeability | ASTM D4491 | 0.01 cm/sec. |

DRAIN ROCK

Shall be free from vegetable matter, lumps, clay, or other objectionable foreign substances.

Shall conform to the following gradation when tested in accordance with ASTM C136:

| Sieve Designation (square openings) | Percentage by Weight Passing Sieves |
| --- | --- |
| 1 1/2 inch | 100 |
| 1 inch | 90-100 |
| 3/8 inch | 25-60 |
| No. 4 | 5-40 |
| No. 8 | 0-20 |

CONTROLLED DENSITY FILL (CDF)

Cement shall be Type I or Type II portland cement conforming to ASTM C150 or blended cements conforming to ASTM C595.

Aggregates shall be non-expansive or reactive with 100 percent passing a 3/8 inch sieve and less than 10 percent passing the No. 200 sieve.  Aggregate shall meet the requirements of ASTM C33.

Fly ash shall conform to ASTM C618, Class F.

Mix CDF ingredients as follows (approximate weight per cubic yard):

| Ingredient | Approximate Weight Per Cubic Yard |
| --- | --- |
| Portland Cement | 100 lbs. (min.) |
| Fly Ash | 300 lbs. |
| Commercial Sand | 1,200 lbs. |
| Commercial Fine Sand | 210 lbs. |
| 3/8 inch Aggregate | 1,450 lbs. |
| Water | 300 lbs. (max) |
| Total Air (percent) | 6% |
| Mix may include pozzolan. Slump shall be between 5 and 10 inches. |

Fill in concrete class below.

SEPTIC TANK AND SEPTIC TANK DISTRIBUTION BOX

See Section 033000, Cast-in-Place Concrete, Class _____.

## EXECUTION

EXCAVATION AND BACKFILL

See Section 312300, Trenching, Backfilling, and Compacting.

EQUIPMENT

Equipment necessary and required for the proper construction of sanitary sewers shall be in good condition to perform the work.

Provide appropriate hoisting equipment to handle pipe in unloading and placing in its final position without damage to the pipe.

Provide such hand tampers and pneumatic tampers to obtain the specified compaction of the pipe bed and backfill.

LAYING PIPE

General:

Inspect pipe for defects prior to laying.  Replace defective pieces at no added cost to the Port.

Lay pipe carefully true to lines and grades on a uniformly firm bed throughout its length.

Pipe which shows undue settlement, is not in true alignment, or is damaged shall be taken up and relaid at no added cost to the Port.

Carefully clean pipe ends and fittings before laying.  Keep pipe ends plugged prior to making connections.

Prevent foreign material (including clothing, tools, debris, etc.) from entering the pipe at all times.

Take adequate precautions to prevent any uplift from occurring to pipe during any interruptions in laying.

Prepare trench to give pipe full length support.

Lower and center pipe in final position.

Laying pipe on blocks not permitted.

Cut pipe only to remove defective ends, to allow insertion of fittings, or to obtain specified lengths.

Anchor bends involving unbalanced pressures with thrust blocks, as shown or directed.

Cast Iron Pipe:  Install in strict accordance to Cast Iron Soil Pipe Institute Standards and Recommendations.

Plastic Pipe

Install in accordance with ASTM D2321.

Split couplings do not provide a watertight joint.

Split Coupling Joints:  Twist or rotate pipe until paint marks on each section line up.

O-Ring Joints:  Align joint and push home utilizing a well-lubricated gasket.  Ensure bedding material is not pulled into the bell.

Pipe designed to handle H-20 wheel loads with 12 inches, minimum, of well-compacted cover.  Heavier loads require additional cover.

Avoid construction traffic over pipe.

Tolerance:  Maximum deviation from true line or grade, as established, shall not exceed 1/2 inch for line and 1/4 inch for grade, provided that such variation does not result in a level or reverse sloping invert.  Measure for grade at the pipe invert, not at the top of the pipe, because of permissible variation in pipe wall thickness.

Backfilling:  See Section 312300, Trenching, Backfilling, and Compacting.

CONNECTIONS

Make connections to existing or proposed structures watertight and smooth for a uniform flow line throughout sewer system.

Grout connections.

UTILITY STRUCTURES

Install as shown on the drawings.

UTILITY WARNING TAPE AND LOCATE WIRE

See Section 312300, Trenching, Backfilling, and Compacting.

SANITARY SEWER SYSTEM TESTING

Notify the Port 48 hours prior to conducting tests.

Backfilling and compaction after testing may damage pipe, pipe alignment, connections, or pipe joints.

Test only after all connections, manholes, backfilling, and compaction is complete between the stations to be tested.

Flush and clean prior to testing and final acceptance.

Hydrostatic or air test all gravity sewers prior to acceptance.

Hydrostatic Test

Air Test

For pipe with inside diameters of 36 inches or greater, individual joints may be tested in lieu of testing an entire section.

Conform to City of Portland Standard Specifications requirements.

Hydrostatic test all pressure sewers (force mains) in accordance with AWWA C600, unless otherwise directed.

Hydrostatic Test

Test pressure shall not be less than 1.25 times the working pressure at the highest point along the test section.

Test shall be at least 2 hours, minimum, duration.

Test pressure shall not vary by more than + 5 psi.

Allowable leakage:

L = SD(P)1/2/133, 200

Where:

L = allowable leakage, in gallons per hour

S = length of pipe tested, in feet

D = nominal diameter of pipe, in inches

P = average test pressure during the test, in pounds per square inch

Repair or replace equipment, materials, or piping found to be defective and/or unsatisfactory.

TELEVISION INSPECTION

Notify the Port when all sewer construction, repairs, and testing is complete.  Allow the Port to witness television inspection and supply the Port with a DVD recording of the television inspection.

If required by the local jurisdiction, the Contractor shall perform a television inspection of the sewer at no additional cost to the Port.

Repair all deficiencies revealed by televiewing at no additional cost to the Port.

FLUSHING AND CLEANING

Clean thoroughly prior to final acceptance.

Flush, if directed.

ABANDONMENT OF EXISTING PIPES, MANHOLES, AND APPURTENANCES

Completely remove all pipe indicated on the drawings.  Remove all manholes and appurtenances to an elevation at least 2 feet below subgrade.

If approved by the Port, manholes may be abandoned in place.

Salvage manhole frames and covers which are suitable for reuse and deliver to a location designated by the Port.

Remove cone or top section of manhole and dispose of off Port property.

Plug the first 12 inches of all pipe entering manhole with non-shrink grout to provide a watertight seal.  Backfill remainder of manhole with controlled density fill (CDF).

If approved by the Port, pipe may be abandoned in place.

Completely fill all voids in the abandoned pipe with controlled density fill (CDF).

Place fill in pipe utilizing low pressure (5 psi, maximum) grouting equipment.

END OF SECTION 333100